# Load Case: Extreme Wind (PGE-Specific — Ground Line Strength)

## Description

PGE-specific extreme wind loading condition for ground-line strength assessment. This is separate from NESC Rule 250C and applies primarily to shorter structures (60 ft and under) and all steel poles. Wood/FRP poles taller than 60 ft are evaluated under Rule 250C instead, not this load case.

## References

- PGE LD20055, Table 2 (extreme wind load and strength factors) - PGE LD20020 (general loading requirements)

## Weather Parameters

Wind speed depends on pole height:

| Pole Height | Wind Speed (mph) | Wind Pressure (psf) |
| --- | --- | --- |
| 60 ft and under | 70 | 12.5 |
| Over 60 ft | 90 | 20.7 |

| Parameter | Value |
| --- | --- |
| Temperature | 60 deg F |
| Ice | None |

Wind pressure is calculated as 0.00256 * V^2 psf and applied via make_environment.

## Load and Strength Factors

PGE LD20055 Table 2:

### Wood / FRP Poles

| Factor | Value |
| --- | --- |
| Wind load factor | 1.0 |
| Wire tension load factor | 1.0 |
| Vertical load factor | 1.0 |
| Strength factor — Wood | 0.75 |
| Strength factor — FRP | 1.0 |

Environment template: PGE_ExtremeWind_Wood

### Steel Poles

| Factor | Value |
| --- | --- |
| Wind load factor | 1.1 |
| Wire tension load factor | 1.1 |
| Vertical load factor | 1.1 |
| Strength factor — Steel | 1.0 |

Environment template: PGE_ExtremeWind_Steel

## Applicability Criteria

| Criterion | Condition |
| --- | --- |
| Pole height 60 ft or under | pole.height <= 60ft |
| OR pole is steel | pole.type.material = "steel" |

Wood/FRP poles taller than 60 ft are excluded — they are covered by Rule 250C instead.

If neither criterion is met, the load case is skipped and the output is null.

## Implementation

- Processing type: portland_nesc~PoleLoadingExtremeWindProcessing - Calculator type: portland_nesc~PoleLoadingExtremeWindCalculator - Wind pressure override: make_environment(template: env, wind_pressure: 0.00256 * V^2 psf) - Simulations: 8 wind directions, non-network solve; only runs when extreme_wind_required is true - Output: Returns environment, wind_speed, worst_pole, worst_stay, worst_xarm; null when not applicable