# portland_nesc — Portland General Electric NESC Overrides

## Overview

The portland_nesc module extends the base nesc module with Portland General Electric (PGE) customer-specific requirements from two design standards:

- LD20055 — Grades of Construction, Load Factors, and Strength Factors - LD20020 — General Loading Requirements for Overhead Lines

PGE rules always apply — there is no toggle. The module follows the same customer-overlay architecture as pacific extends go95.

### Key PGE Deviations from Base NESC

| Area | Base NESC | PGE Override |
| --- | --- | --- |
| Rule 250C — Applicability | Structures/spans > 60 ft only | All structures regardless of height |
| Rule 250C — Wind speed | Grade-dependent (B or C) | Always uses Grade B (85 mph) |
| Rule 250C/D — Load factors | Single set of factors | Steel vs wood/FRP split (different load + strength factors) |
| Rule 250B — Guy checks | Same grade as structure | Always Grade B regardless of structure grade |
| Extreme ice | Not in base NESC | PGE-specific — 0.5"/1.0" ice, no wind |
| Fire wind | Not in base NESC | PGE-specific — 85/110 mph in HFRZs |

## Architecture

### Dependency Chain

portland_nesc~PoleLoadingCheckManager
    |
    |-- rule_242_output        (base nesc — unchanged)
    |-- rule_243_output        (base nesc~PoleLoadingRule243Calculator — unchanged)
    |
    |-- rule_250b_output       (base nesc calculator, PGE processing injected via DI)
    |       |
    |       +-- portland_nesc~PoleLoadingRule250bProcessing
    |               (adds environment_grade_b, simulations_grade_b for guys)
    |
    |-- rule_250c_output       (base nesc calculator, PGE processing injected via DI)
    |       |
    |       +-- portland_nesc~PoleLoadingRule250cProcessing
    |               (all heights, Grade B wind, steel/wood split)
    |
    |-- rule_250d_output       (base nesc — unchanged, PGE factors in env templates)
    |
    |-- rule_277_output        (base nesc — unchanged)
    |
    |-- extreme_ice_output     (PGE-only)
    |       |
    |       +-- portland_nesc~PoleLoadingExtremeIceCalculator
    |               +-- portland_nesc~PoleLoadingExtremeIceProcessing
    |
    +-- fire_wind_output       (PGE-only)
            |
            +-- portland_nesc~PoleLoadingFireWindCalculator
                    +-- portland_nesc~PoleLoadingFireWindProcessing

### Override Strategy

The module uses two override patterns:

1. Dependency Injection (DI): For 250B and 250C, the PGE Processing type is instantiated and injected into the base NESC Calculator via the processing parameter of make_immutable_record. The base Calculator's output formula reads from processing.max_pole, processing.max_stay, etc., so the PGE Processing seamlessly replaces the base Processing without duplicating the Calculator.

2. New types: Extreme ice and fire wind are PGE-only checks with their own Calculator/Processing pairs, following the same structural pattern as base NESC rules.

## File Structure

portland_nesc/
├── module.neara.hjson
├── docs/
│   ├── portland_nesc_module.md               (this file)
│   ├── LD20055_grades_load_strength_factors.md
│   └── LD20020_general_loading_requirements.md
├── Types/
│   ├── portland_nesc~PoleLoadingCheckManager.neara.hjson
│   ├── portland_nesc~PoleLoadingRule250bProcessing.neara.hjson
│   ├── portland_nesc~PoleLoadingRule250cProcessing.neara.hjson
│   ├── portland_nesc~PoleLoadingExtremeIceCalculator.neara.hjson
│   ├── portland_nesc~PoleLoadingExtremeIceProcessing.neara.hjson
│   ├── portland_nesc~PoleLoadingFireWindCalculator.neara.hjson
│   └── portland_nesc~PoleLoadingFireWindProcessing.neara.hjson
└── DataTables/
    ├── portland_nesc~extreme_ice_loading.neara.hjson
    └── portland_nesc~fire_wind_speed.neara.hjson

## CheckManager — `portland_nesc~PoleLoadingCheckManager`

Token: portland_nesc~ct_PoleLoadingCheckManager

Orchestrates all PGE checks. Takes a pole input (type_only ~Pole) and produces outputs for every rule.

| Field | Source | Description |
| --- | --- | --- |
| pole | type_only("~Pole") | Injected pole |
| nesc_pla_model_input | make_immutable_record("nesc~PoleLoadingModelInput", pole: pole) | Shared model input for all rules |
| rule_242_output | Base nesc~PoleLoadingRule242Calculator | Grade of construction per conductor crossings — unchanged |
| rule_243_output | Base nesc~PoleLoadingRule243Calculator | Grade of construction per pole + structure conflict — unchanged |
| rule_250b_output | Base calculator + PGE portland_nesc~PoleLoadingRule250bProcessing injected | Combined ice+wind — guys always Grade B |
| rule_250c_output | Base calculator + PGE portland_nesc~PoleLoadingRule250cProcessing injected | Extreme wind — all heights, Grade B wind, steel/wood |
| rule_250d_output | Base nesc~PoleLoadingRule250dCalculator | Extreme ice+wind — unchanged (PGE factors in env templates) |
| rule_277_output | Base nesc~PoleLoadingRule277Calculator | Insulator strength — unchanged |
| extreme_ice_output | PGE portland_nesc~PoleLoadingExtremeIceCalculator | PGE-only extreme ice (no wind) |
| fire_wind_output | PGE portland_nesc~PoleLoadingFireWindCalculator | PGE-only fire wind in HFRZs |

## Rule 243 — Grade of Construction (Base NESC)

Portland uses the base nesc~PoleLoadingRule243Calculator directly — no PGE override needed. Base NESC Rule 243 provides span-grade aggregation (worst grade across all spans) and structure conflict detection, which covers all PGE requirements. The freeway crossing check on spans covers the major highway criterion.

### Output Structure

{
  grade_of_construction: "B" | "C",
  is_structure_conflict: true | false,
}

## Rule 250B — Combined Ice and Wind Override

### Processing — `portland_nesc~PoleLoadingRule250bProcessing`

Token: portland_nesc~ct_PoleLoadingRule250bProcessing

Extends the base 250B Processing with two new fields to implement LD20055 Table 5: "Guys always Grade B."

| Field | Description |
| --- | --- |
| environment | Standard 250B environment selection by loading district + grade (same as base) |
| environment_grade_b | PGE — Always the Grade B environment for the current loading district |
| simulations | Standard FEA with the grade-appropriate environment |
| simulations_grade_b | PGE — Additional FEA with Grade B environment, runs only when grade = "C" |
| max_pole | Worst pole utilization from simulations (same as base) |
| max_xarm | Worst crossarm utilization from simulations (same as base) |
| max_stay | PGE — Worst stay utilization from simulations_grade_b when available, else simulations |

Logic: When the pole is Grade C, the Processing runs two simulations: 1. Grade C simulation → used for max_pole and max_xarm 2. Grade B simulation → used for max_stay (guys checked at Grade B)

When the pole is Grade B, only one simulation runs and all components use it.

## Rule 250C — Extreme Wind Override

### Processing — `portland_nesc~PoleLoadingRule250cProcessing`

Token: portland_nesc~ct_PoleLoadingRule250cProcessing

Three overrides from base 250C:

| Field | Base NESC | PGE Override |
| --- | --- | --- |
| nesc250c_required | pole.height > 6ft or span.ground_clearance > 60ft | `true` — applies to all structures |
| nesc250c_wind | Grade-dependent wind speed map (dt_250c_grc_wind_speed for C, dt_250c_grb_wind_speed for B) | Always dt_250c_grb_wind_speed (Grade B = 85 mph) |
| environment | Single template "250C C" | Steel/wood split: "PGE_250C_Steel" or "PGE_250C_Wood" based on is_steel_pole |

### Steel/Wood Detection

is_steel_pole: model_input.pole.type.material = "steel"

Used in 250C, extreme ice, and fire wind to select the correct environment template with the appropriate load/strength factors per LD20055.

## Extreme Ice — PGE-Specific

### Calculator — `portland_nesc~PoleLoadingExtremeIceCalculator`

Token: portland_nesc~ct_PoleLoadingExtremeIceCalculator

Thin wrapper that delegates to Processing and shapes output.

### Processing — `portland_nesc~PoleLoadingExtremeIceProcessing`

Token: portland_nesc~ct_PoleLoadingExtremeIceProcessing

Implements LD20055 Table 4 extreme ice (no concurrent wind). This loading condition does not exist in base NESC.

| Field | Description |
| --- | --- |
| extreme_ice_required | true if pole is in heavy or medium loading district |
| ice_params | Lookup from portland_nesc~dt_extreme_ice_loading by loading district |
| is_steel_pole | model_input.pole.type.material = "steel" |
| environment | Template selected by material + district, ice thickness overridden at runtime |
| simulations | Standard FEA with 8 wind directions |
| max_pole / max_stay / max_xarm | Standard worst-case extraction |

### Environment Template Selection

| Pole Material | District | Template |
| --- | --- | --- |
| Wood/FRP | Medium | PGE_ExtremeIce_Wood_Med |
| Wood/FRP | Heavy | PGE_ExtremeIce_Wood_Hvy |
| Steel | Medium | PGE_ExtremeIce_Steel_Med |
| Steel | Heavy | PGE_ExtremeIce_Steel_Hvy |

### Output Structure

{
  environment: <environment record>,
  worst_pole: { check_type, beamreport, simulation, utilisation },
  worst_stay: { stay, check_type, stayreport, simulation, utilisation } | null,
  worst_xarm: { check_type, beamreport, simulation, utilisation },
}

Returns null if extreme_ice_required is false.

## Fire Wind — PGE-Specific

### Calculator — `portland_nesc~PoleLoadingFireWindCalculator`

Token: portland_nesc~ct_PoleLoadingFireWindCalculator

Thin wrapper that delegates to Processing and shapes output.

### Processing — `portland_nesc~PoleLoadingFireWindProcessing`

Token: portland_nesc~ct_PoleLoadingFireWindProcessing

Implements LD20055 Table 4 fire wind loading. Applies to poles in PGE High Fire Risk Zones (HFRZs).

| Field | Description |
| --- | --- |
| fire_wind_required | geo_query against dt_pge_hfrz — true if pole is in a HFRZ |
| is_transmission | max(voltage) >= 57kV |
| is_steel_pole | model_input.pole.type.material = "steel" |
| fire_wind_pressure | Distribution: 0.00256 * 85^2 = 18.5 psf; Transmission: 0.00256 * 110^2 = 31.0 psf |
| environment | "PGE_FireWind_Steel" or "PGE_FireWind_Wood" with wind pressure overridden |
| simulations | Standard FEA with 8 wind directions |
| max_pole / max_stay / max_xarm | Standard worst-case extraction |

### Output Structure

Same shape as extreme ice output. Returns null if fire_wind_required is false (pole not in HFRZ).

## Data Tables

### `portland_nesc~extreme_ice_loading`

Extreme ice parameters by NESC loading district.

| loading_district | temperature_f | ice_thickness_in | wind_pressure_psf |
| --- | --- | --- | --- |
| Medium | 32 | 0.5 | 0 |
| Heavy | 32 | 1.0 | 0 |

### `portland_nesc~fire_wind_speed`

Fire wind speed by voltage class.

| voltage_class | voltage_lower_kv | wind_speed_mph | wind_pressure_psf |
| --- | --- | --- | --- |
| Distribution | 0 | 85 | 18.5 |
| Transmission | 57 | 110 | 31.0 |

## Required Environment Templates

The following environment templates must be created in the Neara model before the module will function. Load and strength factors are defined by LD20055.

### 250C Extreme Wind (LD20055 Table 2)

| Label | Material | Load Factors (all) | Strength Factor |
| --- | --- | --- | --- |
| PGE_250C_Wood | Wood/FRP | 1.0 | Wood=0.75, FRP=1.0 |
| PGE_250C_Steel | Steel | 1.1 | Steel=1.0 |

Wind pressure overridden at runtime via make_environment(template:, wind_pressure:).

### 250D Extreme Ice + Wind (LD20055 Table 3)

| Label | Material | Load Factors (all) | Strength Factor |
| --- | --- | --- | --- |
| PGE_250D_Wood | Wood/FRP | 1.0 | Wood=0.75, FRP=1.0 |
| PGE_250D_Steel | Steel | 1.1 | Steel=1.0 |

Wind pressure and ice overridden at runtime.

### Extreme Ice — No Wind (LD20055 Table 4)

| Label | Material / District | Load Factors | Strength Factor |
| --- | --- | --- | --- |
| PGE_ExtremeIce_Wood_Med | Wood, Medium | wind=1.1, vert=1.1, long=1.0/1.1 | Wood=0.75, FRP=0.75 |
| PGE_ExtremeIce_Wood_Hvy | Wood, Heavy | same | same |
| PGE_ExtremeIce_Steel_Med | Steel, Medium | all=1.1 | Steel=1.0 |
| PGE_ExtremeIce_Steel_Hvy | Steel, Heavy | same | same |

Ice thickness overridden at runtime (Medium=0.5", Heavy=1.0").

### Fire Wind (LD20055 Table 4)

| Label | Material | Load Factors (all) | Strength Factor |
| --- | --- | --- | --- |
| PGE_FireWind_Wood | Wood/FRP | 1.1 | Wood=0.75 |
| PGE_FireWind_Steel | Steel | 1.1 | Steel=1.0 |

Wind pressure overridden at runtime (85 mph=18.5 psf or 110 mph=31.0 psf).

## Required Geospatial Data Tables

| Data Table | Status | Description |
| --- | --- | --- |
| dt_nesc_loading_zones | Existing | NESC loading district boundaries |
| dt_esri_freewaysystem | Existing | Limited-access highway geometries |
| dt_or_railroads | Existing | Railroad geometries |
| dt_nhd_waterbody | Existing | Navigable waterway geometries |
| dt_250c_grb_wind_speed | Existing | 250C Grade B wind speed map |
| dt_250d_ice | Existing | 250D ice thickness map |
| dt_250d_wind | Existing | 250D concurrent wind speed map |
| dt_pge_hfrz | Needed | PGE High Fire Risk Zone boundaries |

Note: If dt_pge_hfrz is not loaded, fire_wind_required returns false and fire wind checks are skipped gracefully.

## FEA Report Field Paths

All processing types extract worst-case results using the same patterns:

| Component | Report Type | Metric | Path |
| --- | --- | --- | --- |
| Pole | BeamReports (filtered: is_on_pole) | Stress | .worst[].normal_stress[].utilization |
| Pole | BeamReports (filtered: is_on_pole) | Moment | .worst[].moment[].utilization |
| Crossarm | BeamReports (filtered: not(is_on_pole)) | Stress | .worst[].normal_stress[].utilization |
| Crossarm | BeamReports (filtered: not(is_on_pole)) | Moment | .worst[].moment[].utilization |
| Stay/Guy | StayCableReports | Tension | .worst[].tension[].utilization |

The higher of stress and moment utilization is reported for poles and crossarms. Stays only report tension.

## Future Enhancements

1. 250D steel/wood split — Create PGE-specific 250D Processing to select PGE_250D_Wood / PGE_250D_Steel templates based on pole material (currently uses base NESC 250D with a single template). 3. FITNES "At Replacement" criteria — Per LD20055, implement deterioration-based analysis using LD40600 parameters. 4. Special loading conditions — Unbalanced longitudinal load, broken conductor, buckle analysis per LD20055 Table 4. 5. PGE Report — Add a portland_nesc-specific PLA report type that includes extreme ice and fire wind results.

## Sync & Compile

dim sync --module portland_nesc --path ./portland_nesc --types all
dim analyze --module portland_nesc 2>&1 | python3 scripts/dim_analyze_filter.py