## CABLE_LAYERS
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDCAB | CHAR |  | Cable ID — foreign key to CABLES |  | Links layer to parent cable
LAYERID | CHAR |  | Layer index (0-based from conductor outward) |  | Ordering of layers radially outward
LAYERTYPE | CHAR |  | Layer type category | e.g. Conductor, Insulation, Shield, Sheath, Jacket, Armour, Bedding, Serving | Identifies which cable component
LAYERNAME | CHAR |  | Layer display name |  | Human-readable layer name from CYMCAP
MATERIAL | INTEGER |  | Material identifier or code |  | Material code or name string
CUSTOM_MATERIAL_NAME | CHAR |  | Custom material name (when material is 'Custom') |  | User-defined material label
THICKNESS | DOUBLE | m | Layer thickness |  | Radial thickness in metres
DIAMETER | DOUBLE | m | Layer outer diameter |  | Outer diameter after this layer
THERMAL_RESIS | DOUBLE | K.m/W | Thermal resistivity of layer material |  | For thermal circuit calculations
INTERNAL_THREE_CORE | INTEGER |  | Internal to 3-core assembly flag | 0=No, 1=Yes | Whether layer is inside the 3-core bundle
TAG | CHAR |  | Record tag |  | Internal flag

## CABLES
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDCAB | VARCHAR |  | Cable ID — unique identifier within CYMCAP |  | Primary key, VARCHAR
CABTITLE | VARCHAR |  | Cable title / description text |  | User-entered label
COMMENTS | VARCHAR |  | Free-text comments |  | User-entered notes
TAG | VARCHAR |  | Record tag (typically 'F') |  | Internal flag; observed value 'F'
INSTALL | SMALLINT |  | Installation / cable type code | 1=Pipe (Triangular), 2=LPOF, 3=Concentric Neutral, 4=Extruded, 5=Other, 6=Combined Sheath | Maps to InstallationType enum per CYMCAP UI
INSTSPEC | SMALLINT |  | Installation specification (currently unused) |  | All values blank in sample DB
CONDMAT | SMALLINT |  | Conductor material code | 1=Copper, 2=Aluminium | Maps to ConductorMaterial enum
CONDCON | SMALLINT |  | Conductor construction code | 1-11: conductor construction code (round stranded, solid, segmental, etc.) | Construction type (round stranded, solid, segmental, etc.)
DRYIMPR | SMALLINT |  | Dry/impregnated insulation flag | 0,1,2,99 | Insulation paper treatment option
CONLOS | SMALLINT |  | Conductor loss calculation option | -1,0,1 | Controls how conductor losses are computed
INSTYP | SMALLINT |  | Insulation type code | -1=Custom, 1=Solid, 2=LPOF, 3=HPOF Self-Contained, 4=HPOF Pipe, 9=EPR, 10=PVC, 11=Polyethylene, 12=XLPE (unfilled), 13=XLPE (filled), 14=Paper | Maps to InsulationType enum
DIELEC | SMALLINT |  | Dielectric loss option | -3=Enter tan delta & epsilon, -1=Enter tan delta, 0=Program selects | Maps to DielectricOption enum
NUMCON | SMALLINT |  | Number of conductors (legacy, appears unused) | 1=Single Core, 3=Three Core | See NUMBCON instead
SKIDCON | SMALLINT |  | Concentric/skid wire material code | -1=Custom, 0=None, 1=Copper, 2=Brass/Bronze, 3=Zinc, 4=Stainless Steel | Maps to ConcentricNeutralMaterial enum
SKNROUNDWI | SMALLINT |  | Concentric wire construction type | 1=Round Wires, 2=Flat Straps | Round wires vs flat straps
SHEAMAT | SMALLINT |  | Sheath material code | 0=None, 1=Aluminium, 2=Lead, 3=Lead w/ Reinforcing, 4=Copper | Maps to SheathMaterial enum
CORRUG | SMALLINT |  | Corrugation type | 1=Non-corrugated, 2=Corrugated, 3=Longitudinally Applied Tape | Maps to CorrugationType enum
BONDING | SMALLINT |  | Bonding configuration (currently unused) |  | All values blank in sample DB
LOSFACT | SMALLINT |  | Loss factor override (currently unused) |  | All values blank in sample DB
JACKMAT | SMALLINT |  | Jacket material code | -1=Custom, 0=None, 1=Compound Jute, 2=Rubber Sandwich, 3=Polychloroprene, 4=Polyethylene, 5=PVC, 6=EPR, 7=Butyl Rubber, 8=Coal Tar Rubber | Maps to JacketMaterial enum
ARMREIN | SMALLINT |  | Armour type code | -4=Custom non-mag tape, -3=Custom mag wire/tape, -1=Custom non-mag wire, 0=None, 1=Steel wire touching, 2=Steel wire not touching, 3=Steel tape, 4=Copper wire, 5=Stainless steel wire, 6=TECK | Maps to ArmourType enum
ARMBED | SMALLINT |  | Armour bedding material code | -1=Custom, 0=None, 1=Compounded Jute, 2=Rubber Sandwich | Maps to ArmourBedding enum
PERMEAB | SMALLINT |  | Relative permeability of armour |  | Typically 0 (program default); for magnetic armour
ARMSERV | SMALLINT |  | Armour serving material code | -1=Custom, 0=None, 1=Compounded Jute | Maps to ArmourServing enum
INSUSHI | SMALLINT |  | Insulation screen type | 0=No Screen, 1=Belted (unscreened), 2=Semiconductive, 3=Copper Tape, 4=Aluminium Tape | Maps to InsulationScreenType enum
TAPINPIP | SMALLINT |  | Reinforcing tape over insulation screen material | 0=None, 2=Brass/Bronze, 4=Stainless Steel, 5=Steel | Material code for sheath reinforcing tape
OVERSHEATH | SMALLINT |  | Oversheath flag (currently unused) |  | All zeros in sample DB
TRANSPO | SMALLINT |  | Transposition flag (currently unused) |  | All blank in sample DB
PIPCONFI | SMALLINT |  | Pipe configuration | 0=N/A, 1=Triangular, 2=Cradled | Triangular vs cradled for pipe-type cables
PIPEMAT | SMALLINT |  | Pipe material code (currently unused) |  | Not populated in sample DB
DUCTBANK | SMALLINT |  | Duct bank reference (currently unused) |  | Not populated in sample DB
MINSECLE | SMALLINT |  | Minimum section length (currently unused) |  | Not populated in sample DB
SECSPAC | SMALLINT |  | Section spacing (currently unused) |  | Not populated in sample DB
NSEGMENTS | SMALLINT |  | Number of segments for FEM meshing | 1,6 | Conductor mesh subdivision
BRATIO | DOUBLE |  | Beta ratio (bundle conductor ratio) |  | Typically 1.0
RHC | DOUBLE | K.m/W | Custom conductor thermal resistivity |  | Zero = program default
ALFAC | DOUBLE | 1/K | Conductor resistance temperature coefficient |  | Zero = program default
AKP | DOUBLE |  | Proximity effect factor kp (IEC 60287-1-1) |  | 0 = program selects; manual override for AC resistance
AKS | DOUBLE |  | Skin effect factor ks (IEC 60287-1-1) |  | 0 = program selects; 0.001 stored when GUI shows 0.0
RHI | DOUBLE | K.m/W | Custom insulation thermal resistivity |  | Used when INSTYP=-1 (custom)
COSPHI | DOUBLE |  | Insulation dielectric loss tangent (tan delta) |  | Custom value used when DIELEC=-1 or -3
EPSILN | DOUBLE |  | Insulation relative permittivity (epsilon_r) |  | Custom value used when DIELEC=-3
RHK | DOUBLE | ohm.m | Custom concentric neutral wire electrical resistivity |  | Used when SKIDCON=-1 (custom)
ALFAK | DOUBLE | 1/K | Concentric neutral resistance temperature coefficient |  | Per K at 20°C
RHS | DOUBLE | ohm.m | Custom sheath electrical resistivity |  | Zero = program default for selected material
ALFAS | DOUBLE | 1/K | Sheath resistance temperature coefficient |  | Zero = program default
ALOS | DOUBLE |  | Additional losses factor (currently unused) |  | All blank in sample DB
RHJ | DOUBLE | K.m/W | Custom jacket thermal resistivity |  | Used when JACKMAT=-1 (custom)
RHA | DOUBLE | ohm.m | Custom armour electrical resistivity at 20°C |  | Value in Ω·m (e.g. 1.38e-7)
ALFAA | DOUBLE | 1/K | Armour resistance temperature coefficient at 20°C |  | Per K
RHB | DOUBLE | K.m/W | Armour bedding thermal resistivity |  | Used when ARMBED=-1 (custom)
AME | DOUBLE |  | Unknown material parameter (always 0) |  | Currently zero for everything
AMT | DOUBLE |  | Unknown material parameter (always 0) |  | Currently zero for everything
GAMMA | DOUBLE |  | Unknown material parameter (always 0) |  | Currently zero for everything
RHAS | DOUBLE | K.m/W | Armour serving thermal resistivity |  | Used when ARMSERV=-1 (custom)
RHT | DOUBLE | K.m/W | Unknown thermal resistivity (always 0) |  | Currently zero for everything
ALFAT | DOUBLE | 1/K | Unknown temperature coefficient (always 0) |  | Currently zero for everything
RHO | DOUBLE |  | Unknown resistivity parameter (always 0) |  | Currently zero for everything
PIPFAC | DOUBLE |  | Pipe factor (currently unused) |  | All blank in sample DB
AM | DOUBLE |  | Unknown parameter (currently unused) |  | All blank in sample DB
AN | DOUBLE |  | Unknown parameter (currently unused) |  | All blank in sample DB
NSECT | SMALLINT |  | Number of sections (currently unused) |  | All blank in sample DB
RHD | DOUBLE |  | Unknown thermal resistivity (currently unused) |  | All blank in sample DB
NUMBCON | SMALLINT |  | Number of cores/conductors | 1=Single Core, 3=Three Core | 1=Single Core, 3=Three Core
CONAREA | DOUBLE | m² | Conductor cross-sectional area |  | Standard cable conductor area in m²
CONDIAM | DOUBLE | m | Conductor outer diameter |  | Diameter in metres
CONSHDI | DOUBLE | m | Diameter over conductor shield |  | Outer diameter after conductor shield layer
CONSPAC | DOUBLE | m | Three-core cable conductor spacing diameter |  | Diameter after individual cores in 3-core cable
CONINDI | DOUBLE | m | Conductor inner diameter (hollow core) |  | For hollow-core/oil-channel conductors
CONEQDI | DOUBLE | m | Conductor equivalent diameter |  | Used for sector-shaped conductors
CENTRDIS | DOUBLE | m | Centre distance between conductors |  | Only populated for specific cable types
RADCIRC | DOUBLE | m | Radius of circle through 3-core conductors |  | For 3-core sector-shaped cables
VOLTAGE | DOUBLE | V | Rated voltage |  | Phase-to-ground voltage in Volts
INSUDIA | DOUBLE | m | Insulation outer diameter |  | Diameter over insulation in metres
INSHIDI | DOUBLE | m | Insulation inner (shield) diameter |  | Inner diameter of insulation screen layer
INSTHIC | DOUBLE | m | Insulation thickness |  | For 3-core: 2× insulation thickness
CINSSHTH | DOUBLE | m | Common insulation screen thickness (3-core) |  | 2× insulation screen thickness for 3-core cables
INSSHTH | DOUBLE | m | Insulation screen thickness (individual) |  | Per-core insulation screen thickness
MESHITH | DOUBLE | m | Metallic insulation screen thickness |  | Thickness of metallic insulation screen
CIRCIRDI | DOUBLE | m | Unknown diameter (rare usage) |  | Only populated in one cable (case 51)
SHEATHDI | DOUBLE | m | Sheath outer diameter |  | Metallic sheath outer diameter in metres
SHETHIC | DOUBLE | m | Sheath thickness |  | Metallic sheath thickness in metres
SHINRAD | DOUBLE | m | Corrugated sheath inner radius |  | Inner trough radius for corrugated sheaths
SHOUTRAD | DOUBLE | m | Corrugated sheath outer radius |  | Outer crest radius for corrugated sheaths
TAPBIND | DOUBLE | m | Tape over insulation screen — outer diameter |  | Diameter after tape application
TAPBINTH | DOUBLE | m | Tape over insulation screen — thickness |  | Tape thickness in metres
TAPBINWI | DOUBLE | m | Tape over insulation screen — width |  | Tape width in metres
TAPENUM | SMALLINT |  | Number of tapes over insulation screen |  | Integer count
LAYLENG | DOUBLE | m | Tape lay length |  | Helical lay length of tape
LAYLENG1 | DOUBLE | m | Tape lay length (secondary, unclear usage) |  | Purpose unclear
OVSHETDI | DOUBLE | m | Armour bedding outer diameter |  | Diameter after armour bedding; rarely populated
OVSHETH | DOUBLE | m | Armour bedding thickness (alternative) |  | Rarely populated
JACKDIA | DOUBLE | m | Jacket outer diameter |  | Non-metallic jacket outer diameter
JACKTHI | DOUBLE | m | Jacket thickness |  | Non-metallic jacket thickness
ARMBEDTH | DOUBLE | m | Armour bedding thickness |  | Bedding layer thickness in metres
ARMSERTH | DOUBLE | m | Armour serving thickness |  | Serving layer thickness in metres
SKINEUDI | DOUBLE | m | Diameter over concentric neutral wires |  | Outer diameter after concentric wire layer
SKNSTRAPLG | DOUBLE | m | Concentric neutral strap width |  | Width of flat strap (when flat straps selected)
WIARMDIA | DOUBLE | m | Diameter over wire armour |  | Outer diameter after armour wire layer
TAPARMDI | DOUBLE | m | Diameter over tape armour |  | Outer diameter after armour tape layer
SKNEWIDI | DOUBLE | m | Concentric neutral wire diameter |  | Individual wire diameter
ARMWIRDI | DOUBLE | m | Armour wire diameter |  | Individual armour wire diameter
TAPARMAR | DOUBLE | m² | Armour tape cross-sectional area |  | For tape armour where width not separately defined
SKNEWILE | DOUBLE | m | Concentric neutral wire lay length |  | Helical lay length
ARMWIRLE | DOUBLE | m | Armour wire lay length |  | Helical lay length
SKNEWINU | SMALLINT |  | Number of concentric neutral wires |  | Integer count
ARMWIRNU | SMALLINT |  | Number of armour wires |  | Integer count
OVERDIAM | DOUBLE | m | Overall cable outer diameter |  | Final outer diameter of complete cable
DUPIINDI | DOUBLE | m | Duct/pipe inner diameter (currently unused) |  | Not populated in sample DB
DUPIOTDI | DOUBLE | m | Duct/pipe outer diameter (currently unused) |  | Not populated in sample DB
SLCSHTH | SMALLINT |  | Sheath configuration for 3-core cables | 1=Individual, 2=Common | Whether sheath is per-core or common
SLCCONC | SMALLINT |  | Concentric wire configuration for 3-core cables | 1=Individual, 2=Common | Whether concentric wires are per-core or common
CORRUGHGT | DOUBLE | m | Corrugation height |  | Height of corrugation on corrugated sheath
TAPOVERLAP | DOUBLE | m | Tape overlap |  | Overlap distance for helically applied tapes
TAPWIDTH | DOUBLE | m | Tape width |  | Width of reinforcing/screen tape
TAPTH | DOUBLE | m | Tape thickness |  | Thickness of reinforcing/screen tape
ACCFACTOR | DOUBLE |  | Accumulation factor |  | Purpose unclear; possibly for bundled cables
DCRESIS | DOUBLE | ohm/m | DC resistance at 20°C |  | Conductor DC resistance per metre
DOVLCSHLD | DOUBLE | m | Diameter over longitudinal cable shield |  | Only for longitudinally applied tapes
LOCKEDBY | VARCHAR |  | Locked by user (currently unused) |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp (currently unused) |  | Multi-user locking timestamp
CONDCNAM | VARCHAR |  | Custom conductor material name |  | Text label for custom conductor
INSUCNAM | VARCHAR |  | Custom insulation material name |  | Text label for custom insulation
SHTHCNAM | VARCHAR |  | Custom sheath material name |  | Text label for custom sheath
REINFCNAM | VARCHAR |  | Custom reinforcing tape material name |  | Text label for custom reinforcing
SKIDCNAM | VARCHAR |  | Custom concentric/skid wire material name |  | Text label for custom wire material
OVSHTHCNAM | VARCHAR |  | Custom oversheath material name |  | Text label
ARMBEDCNAM | VARCHAR |  | Custom armour bedding material name |  | Text label
ARMOURCNAM | VARCHAR |  | Custom armour material name |  | Text label
ARMSRVCNAM | VARCHAR |  | Custom armour serving material name |  | Text label
JACKETCNAM | VARCHAR |  | Custom jacket material name |  | Text label
SS_TEMP | SMALLINT | °C | Maximum steady-state conductor temperature |  | IEC 60287 maximum operating temperature
TR_TEMP | SMALLINT | °C | Maximum transient/emergency conductor temperature |  | IEC 60853 emergency rating temperature
MSTR_IDCAB | VARCHAR |  | Master cable ID reference (currently unused) |  | Not populated in sample DB
ShCctConductorData | VARCHAR |  | Short-circuit conductor data (CSV string) |  | Format: rho,alpha,maxT,duration,flag
ShCctSheathData | VARCHAR |  | Short-circuit sheath data (CSV string) |  | Format: rho,alpha,maxT,duration,flag
ShCctReinforcingTapeData | VARCHAR |  | Short-circuit reinforcing tape data (CSV string) |  | Format: rho,alpha,maxT,duration,flag
ShCctSkidConcentricData | VARCHAR |  | Short-circuit concentric/skid data (CSV string) |  | Format: rho,alpha,maxT,duration,flag
ShCctArmourData | VARCHAR |  | Short-circuit armour data (CSV string) |  | Format: rho,alpha,maxT,duration,flag
ShCctPipeCoatingMaterial | INTEGER |  | Short-circuit pipe coating material |  | Not populated
ShCctPipeCoatingCustomRHJ | DOUBLE | K.m/W | Custom pipe coating thermal resistivity |  | Not populated
ShCctPipeMaterial | INTEGER |  | Short-circuit pipe material code |  | Not populated
ShCctPipeFactor | DOUBLE |  | Short-circuit pipe factor |  | Not populated
ShCctInsideDuctDiam | DOUBLE | m | Short-circuit inside duct diameter |  | Not populated
ShCctOutsideDuctDiam | DOUBLE | m | Short-circuit outside duct diameter |  | Not populated
ShCctOverallDuctDiam | DOUBLE | m | Short-circuit overall duct diameter |  | Not populated
FillersSameAsInsuFlag | INTEGER |  | Filler material same-as-insulation flag | -99=No Fillers, 0=Custom, 1=Same as insulation | For 3-core cable fillers
FillersResis | DOUBLE | K.m/W | Filler thermal resistivity |  | Custom filler thermal resistivity
NbrOfWiresComposingStrandedConductor | INTEGER |  | Number of strands in conductor |  | Used for inductance calculations
WireGauge | INTEGER |  | Wire gauge selection code |  | Concentric wire gauge; affects thickness/diameter
CasingInsideDiam | DOUBLE | m | Casing inside diameter (unused) |  | Not populated
CasingOutsideDiam | DOUBLE | m | Casing outside diameter (unused) |  | Not populated
CasingConst | INTEGER |  | Casing construction code (unused) |  | Not populated
CasingRh | DOUBLE | K.m/W | Casing thermal resistivity (unused) |  | Not populated
CasingFormation | INTEGER |  | Casing formation code (unused) |  | Not populated
ArmourEmbeddedPEInnerTh | DOUBLE | m | PE/AL/PE armour — inner PE thickness |  | For PE/AL/PE laminate armour
ArmourEmbeddedAluminumTh | DOUBLE | m | PE/AL/PE armour — aluminium thickness |  | For PE/AL/PE laminate armour
ArmourEmbeddedPEOuterTh | DOUBLE | m | PE/AL/PE armour — outer PE thickness |  | For PE/AL/PE laminate armour
PrintingCompactCompressedFlag | INTEGER |  | Compact vs compressed conductor label flag | 0=Compressed, 1=Compact | Display label only
SideBySidePictFileName | VARCHAR |  | Side-by-side picture filename (GUI) |  | GUI display field
SideBySidePictScaleIndex | INTEGER |  | Picture scale index (GUI) |  | GUI display field
DataSheetFileNames | LONGCHAR |  | Attached data sheet filenames (GUI) |  | GUI display field
GMRConductor | DOUBLE | m | Geometric mean radius — conductor |  | For impedance calculations
GMRSheath | DOUBLE | m | Geometric mean radius — sheath |  | For impedance calculations
GMRConcentricNeutral | DOUBLE | m | Geometric mean radius — concentric neutral |  | For impedance calculations
LongestSection | DOUBLE | m | Longest bonding section length |  | For cross-bonding calculations
LongerSection | DOUBLE | m | Longer bonding section length |  | For cross-bonding calculations
ShortestSection | DOUBLE | m | Shortest bonding section length |  | For cross-bonding calculations
BETAC | DOUBLE | J/(m³·K) | Conductor volumetric thermal capacitance |  | IEC 60853 transient parameter
SHC | DOUBLE | J/(kg·K) | Conductor specific heat capacity |  | IEC 60853 transient parameter
BETAS | DOUBLE | J/(m³·K) | Sheath volumetric thermal capacitance |  | IEC 60853 transient parameter
SHS | DOUBLE | J/(kg·K) | Sheath specific heat capacity |  | IEC 60853 transient parameter
BETAT | DOUBLE | J/(m³·K) | Reinforcing tape volumetric thermal capacitance |  | IEC 60853 transient parameter
SHT | DOUBLE | J/(kg·K) | Reinforcing tape specific heat capacity |  | IEC 60853 transient parameter
BETAK | DOUBLE | J/(m³·K) | Concentric neutral volumetric thermal capacitance |  | IEC 60853 transient parameter
SHK | DOUBLE | J/(kg·K) | Concentric neutral specific heat capacity |  | IEC 60853 transient parameter
BETAA | DOUBLE | J/(m³·K) | Armour volumetric thermal capacitance |  | IEC 60853 transient parameter
SHA | DOUBLE | J/(kg·K) | Armour specific heat capacity |  | IEC 60853 transient parameter
Dimension_correction_flag | INTEGER |  | Dimension correction flag | 0,2 | Purpose unclear
Duct_custom_U | DOUBLE |  | Custom duct parameter U (unused) |  | Not populated
Duct_custom_V | DOUBLE |  | Custom duct parameter V (unused) |  | Not populated
Duct_custom_Y | DOUBLE |  | Custom duct parameter Y (unused) |  | Not populated
JACKETMAT_SLTYPE | INTEGER |  | Per-core jacket material code (3-core) | -1=Custom, 0=None, 1=Compound Jute, 2=Rubber Sandwich, 3=Polychloroprene, 4=Polyethylene, 5=PVC, 6=EPR, 7=Butyl Rubber, 8=Coal Tar Rubber | Jacket around each individual core
JACKETCNAM_SLTYPE | VARCHAR |  | Per-core custom jacket material name |  | Text label
RHJ_SLTYPE | DOUBLE | K.m/W | Per-core custom jacket thermal resistivity |  | For individual core jackets
JACKET_THI_SLTYPE | DOUBLE | m | Per-core jacket thickness |  | Only for specific cable types (e.g. city cable)
GROUP_CABLE_NAME | VARCHAR |  | Cable group/folder name |  | Organizational folder in CYMCAP UI
K_SpecificInsulationResis | DOUBLE | M.ohm.km | K factor for insulation resistance |  | Specific insulation resistance
Frequency_flag | INTEGER |  | Frequency calculation flag (unused) |  | Not populated
Frequency | DOUBLE | Hz | System frequency (cable-level override) |  | Not populated; typically set at study level
INSSYS | INTEGER |  | Insulation system code | 1,2 | Purpose unclear
MILWIRECON | INTEGER |  | Milliken wire construction type | 1=Insulated, 2=Unidirectional, 3=Bidirectional | For Milliken conductors
MEDIUM_DUCT_FLAG | INTEGER |  | Medium/duct flag (unused) |  | Not populated
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property flag (unused) |  | Not populated
OUTER_CABLE_PHASE_FLAG | INTEGER |  | Outer cable phase flag (unused) |  | Not populated
CONDSHLDMAT | INTEGER |  | Conductor shield material code | -1=Custom, 0=Same as insulation, 15=Semiconductive, 99=Undefined | Maps to ConductorShieldMaterial enum
RHCS | DOUBLE | K.m/W | Custom conductor shield thermal resistivity |  | Used when CONDSHLDMAT=-1 (custom)
CONDSHLDCNAM | CHAR |  | Custom conductor shield material name |  | Text label
CORE_LENGTH_OF_LAY | DOUBLE | m | Core length of lay (3-core cables) |  | Helical lay length of individual cores
LENGTH_OF_PITCH | DOUBLE | m | Corrugated sheath pitch length |  | Corrugation pitch for corrugated sheaths
ARMROUNDWI | INTEGER |  | Armour wire shape flag | 0=N/A, 1=Round Wire, 2=Flat Straps | Wire vs strap armour
ARMSTRAPLG | DOUBLE | m | Armour strap width |  | Width of flat strap armour
ACDC_FLAG | INTEGER |  | AC/DC flag | 0=AC, 1=DC | Maps to AcDcFlag enum
ARMREIN2 | INTEGER |  | Second armour type code (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMBED2 | INTEGER |  | Second armour bedding material (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMBEDTH2 | DOUBLE |  | Second armour bedding thickness (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMBED_DIAM2 | DOUBLE |  | Second armour bedding diameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMWIRDI2 | DOUBLE |  | Second armour wire diameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
WIARMDIA2 | DOUBLE |  | Second armour outer diameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
TAPARMAR2 | DOUBLE |  | Second armour tape area (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMWIRLE2 | DOUBLE |  | Second armour wire lay length (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
TAPARMDI2 | DOUBLE |  | Second armour tape diameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMWIRNU2 | INTEGER |  | Second armour wire count (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMROUNDWI2 | INTEGER |  | Second armour wire shape (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMSTRAPLG2 | DOUBLE |  | Second armour strap width (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ArmourEmbeddedPEInnerTh2 | DOUBLE |  | Second armour PE inner thickness (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ArmourEmbeddedAluminumTh2 | DOUBLE |  | Second armour aluminium thickness (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ArmourEmbeddedPEOuterTh2 | DOUBLE |  | Second armour PE outer thickness (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
PERMEAB2 | INTEGER |  | Second armour permeability (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
RHA2 | DOUBLE |  | Second armour resistivity (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ALFAA2 | DOUBLE |  | Second armour temp coefficient (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
BETAA2 | DOUBLE |  | Second armour thermal capacitance (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
SHA2 | DOUBLE |  | Second armour specific heat (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
RHB2 | DOUBLE |  | Second armour bedding thermal resistivity (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
AME2 | DOUBLE |  | Second armour AME parameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
AMT2 | DOUBLE |  | Second armour AMT parameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
GAMMA2 | DOUBLE |  | Second armour GAMMA parameter (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMBEDCNAM2 | CHAR |  | Second armour bedding custom material name (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
ARMOURCNAM2 | CHAR |  | Second armour custom material name (second armour layer — not populated) |  | For double-armoured cables; not used in sample DB
CITYCABLE_FLAG | INTEGER |  | Retrofitted city cable flag | 1=City cable (e.g. CIGRE Case 9) | Indicates special city cable configuration
ShCctSecondArmourData | CHAR |  | Short-circuit second armour data (CSV string) |  | For double-armoured cables

## STUDCAB_LAYERS
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case identifier
IDCAB | CHAR |  | Cable ID — foreign key to CABLES |  | Same as CABLE_LAYERS.IDCAB; Links layer to parent cable
LAYERID | CHAR |  | Layer index (0-based from conductor outward) |  | Same as CABLE_LAYERS.LAYERID; Ordering of layers radially outward
LAYERTYPE | CHAR |  | Layer type category | e.g. Conductor, Insulation, Shield, Sheath, Jacket, Armour, Bedding, Serving | Same as CABLE_LAYERS.LAYERTYPE; Identifies which cable component
LAYERNAME | CHAR |  | Layer display name |  | Same as CABLE_LAYERS.LAYERNAME; Human-readable layer name from CYMCAP
MATERIAL | INTEGER |  | Material identifier or code |  | Same as CABLE_LAYERS.MATERIAL; Material code or name string
CUSTOM_MATERIAL_NAME | CHAR |  | Custom material name (when material is 'Custom') |  | Same as CABLE_LAYERS.CUSTOM_MATERIAL_NAME; User-defined material label
THICKNESS | DOUBLE | m | Layer thickness |  | Same as CABLE_LAYERS.THICKNESS; Radial thickness in metres
DIAMETER | DOUBLE | m | Layer outer diameter |  | Same as CABLE_LAYERS.DIAMETER; Outer diameter after this layer
THERMAL_RESIS | DOUBLE | K.m/W | Thermal resistivity of layer material |  | Same as CABLE_LAYERS.THERMAL_RESIS; For thermal circuit calculations
INTERNAL_THREE_CORE | INTEGER |  | Internal to 3-core assembly flag | 0=No, 1=Yes | Same as CABLE_LAYERS.INTERNAL_THREE_CORE; Whether layer is inside the 3-core bundle
TAG | CHAR |  | Record tag |  | Same as CABLE_LAYERS.TAG; Internal flag

## CABLES_INST
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IdStudy | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links installation to parent study
Execuno | SMALLINT |  | Execution number within study |  | Sub-case identifier
CabIndex | SMALLINT |  | Cable position index (0-based) |  | Order of cable within installation layout
FeederId | VARCHAR |  | Feeder identifier |  | Circuit/feeder grouping label
Circuit | SMALLINT |  | Circuit number |  | 1-based circuit index
PhaseId | VARCHAR |  | Phase identifier |  | e.g. 'A', 'B', 'C' or '1', '2', '3'
IdCab | VARCHAR |  | Cable ID — foreign key to CABLES |  | Which cable design is installed here
XL | DOUBLE | m | Horizontal position |  | X coordinate of cable centre
YL | DOUBLE | m | Vertical position (depth, negative = underground) |  | Y coordinate (depth below surface)
AmpTemp | DOUBLE | °C | Maximum conductor temperature for ampacity |  | Temperature limit for this installation point
RefFrac | DOUBLE |  | Reference fraction |  | Fraction of reference current
LoadFactor | DOUBLE |  | Load factor |  | Ratio of average to peak load
Layout | VARCHAR |  | Layout identifier |  | Layout configuration string
DuctNo | SMALLINT |  | Duct number (0 = direct buried) |  | Which duct in a duct bank (0 if none)
Positions | VARCHAR |  | Cable positions data (serialized) |  | Internal layout data
LayerIndexNo | SMALLINT |  | Soil/backfill layer index |  | Which thermal layer this cable is in
XL_CenterOfDuctsInTrefoil | DOUBLE | m | X centre of trefoil duct group |  | For trefoil duct arrangements
YL_CenterOfDuctsInTrefoil | DOUBLE | m | Y centre of trefoil duct group |  | For trefoil duct arrangements
Label_X | DOUBLE | px | Label X position (GUI) |  | GUI display coordinate
Label_Y | DOUBLE | px | Label Y position (GUI) |  | GUI display coordinate
Label_Width | DOUBLE | px | Label width (GUI) |  | GUI display size
Label_Height | DOUBLE | px | Label height (GUI) |  | GUI display size
Label_AMP_A | DOUBLE |  | Label ampacity phase A text (GUI) |  | GUI display
Label_TEMP_A | DOUBLE |  | Label temperature phase A text (GUI) |  | GUI display
Label_AMP_B | DOUBLE |  | Label ampacity phase B text (GUI) |  | GUI display
Label_TEMP_B | DOUBLE |  | Label temperature phase B text (GUI) |  | GUI display
Label_AMP_C | DOUBLE |  | Label ampacity phase C text (GUI) |  | GUI display
Label_TEMP_C | DOUBLE |  | Label temperature phase C text (GUI) |  | GUI display
Label_Align_Hor | INTEGER |  | Label horizontal alignment (GUI) |  | GUI display
Label_Align_Ver | INTEGER |  | Label vertical alignment (GUI) |  | GUI display
Label_Bgd_Color | INTEGER |  | Label background colour (GUI) |  | GUI display
Label_Font_Color | INTEGER |  | Label font colour (GUI) |  | GUI display
Label_Connected_Line | INTEGER |  | Label connector line flag (GUI) |  | GUI display
NbCables_per_duct | INTEGER |  | Number of cables per duct |  | For multiple cables in single duct
YEARLY_LOADFACTOR | DOUBLE |  | Yearly load factor |  | Annual average/peak ratio
WEEKLY_LOADFACTOR | DOUBLE |  | Weekly load factor |  | Weekly average/peak ratio
ANGLE | DOUBLE | ° | Cable installation angle |  | Rotation angle of cable group
SUBLAYOUT | VARCHAR |  | Sub-layout identifier |  | Layout subdivision
LABEL_CUSTOMIZE_VERSION | INTEGER |  | Label customization version (GUI) |  | GUI version tracking
LABEL_TEXT_LANGUAGE | INTEGER |  | Label text language (GUI) |  | GUI localisation
LABEL_SHOW_CIRCUITNO | INTEGER |  | Show circuit number in label (GUI) |  | GUI display toggle
LABEL_CIRCUITNO_ORDER | INTEGER |  | Circuit number display order (GUI) |  | GUI display order
LABEL_SHOW_FEEDERID | INTEGER |  | Show feeder ID in label (GUI) |  | GUI display toggle
LABEL_FEEDERID_ORDER | INTEGER |  | Feeder ID display order (GUI) |  | GUI display order
LABEL_SHOW_CABLEID | INTEGER |  | Show cable ID in label (GUI) |  | GUI display toggle
LABEL_CABLEID_ORDER | INTEGER |  | Cable ID display order (GUI) |  | GUI display order
LABEL_SHOW_PHASE | INTEGER |  | Show phase in label (GUI) |  | GUI display toggle
LABEL_PHASE_ORDER | INTEGER |  | Phase display order (GUI) |  | GUI display order
LABEL_SHOW_LOAD_FACTOR | INTEGER |  | Show load factor in label (GUI) |  | GUI display toggle
LABEL_LOAD_FACTOR_ORDER | INTEGER |  | Load factor display order (GUI) |  | GUI display order
LABEL_SHOW_ANGLE | INTEGER |  | Show angle in label (GUI) |  | GUI display toggle
LABEL_ANGLE_ORDER | INTEGER |  | Angle display order (GUI) |  | GUI display order
LABEL_SHOW_FREQUENCY | INTEGER |  | Show frequency in label (GUI) |  | GUI display toggle
LABEL_FREQUENCY_ORDER | INTEGER |  | Frequency display order (GUI) |  | GUI display order
LABEL_FONT_SIZE | INTEGER | pt | Label font size (GUI) |  | GUI display
LABEL_SHOW_CABLE_VOLTAGE | INTEGER |  | Show cable voltage in label (GUI) |  | GUI display toggle
LABEL_CABLE_VOLTAGE_ORDER | INTEGER |  | Cable voltage display order (GUI) |  | GUI display order
LABEL_SHOW_CABLE_SIZE | INTEGER |  | Show cable size in label (GUI) |  | GUI display toggle
LABEL_CABLE_SIZE_ORDER | INTEGER |  | Cable size display order (GUI) |  | GUI display order
AMPTEMP_EXTRA | DOUBLE |  | Extra ampacity/temperature data |  | Additional calc data
RTTR_STATUSFLAG | INTEGER |  | Real-time thermal rating status flag |  | RTTR module status
TREFOIL_DISTANCE | DOUBLE | m | Distance between trefoil cables |  | Spacing for trefoil arrangement
MCPP_STATUS_FLAG | CHAR |  | MCPP module status flag |  | Multi-cable per phase status
REFER_CABLE_DEPTH_FLAG | INTEGER |  | Reference cable depth flag |  | Depth reference method
MAX_INSU_TEMP_DROP | DOUBLE | °C | Maximum insulation temperature drop |  | Insulation thermal constraint
XL_3D | DOUBLE | m | 3D X position |  | For 3D visualisation
ZL_3D | DOUBLE | m | 3D Z position |  | For 3D visualisation
SHOWAXIS_3D_FLAG | INTEGER |  | Show 3D axis flag (GUI) |  | GUI display toggle
MULTIPTS_3D_X | CHAR |  | 3D multi-point X coordinates |  | For 3D cable routing
MULTIPTS_3D_Y | CHAR |  | 3D multi-point Y coordinates |  | For 3D cable routing
MULTIPTS_3D_Z | CHAR |  | 3D multi-point Z coordinates |  | For 3D cable routing
MULTIPTS_3D_BRADIUS | CHAR | m | 3D multi-point bend radius |  | For 3D cable routing
ORIGIN_STARTING_PTS_XYZ | CHAR |  | 3D origin starting points |  | For 3D cable routing
RELATIVE_POS_3D | CHAR |  | 3D relative position |  | For 3D cable routing

## DAYWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYLOAD | VARCHAR |  | Load window ID — foreign key to LOADWIN |  | Links day to parent load window
KEYSHAPE | VARCHAR |  | Shape ID — foreign key to SHAPEWIN |  | Which daily shape to use
SF | DOUBLE |  | Scale factor for this day |  | Multiplier on base amps for this day
ORDER_NO | VARCHAR |  | Day order number within load window |  | Sequence position
TAG | VARCHAR |  | Record tag |  | Internal flag

## STUDCAB
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | SMALLINT |  | Execution number |  | Sub-case identifier
CABTITLE | VARCHAR |  | Cable title / description text |  | Same as CABLES.CABTITLE; User-entered label
IDCAB | VARCHAR |  | Cable ID — unique identifier within CYMCAP |  | Same as CABLES.IDCAB; Primary key, VARCHAR
COMMENTS | VARCHAR |  | Free-text comments |  | Same as CABLES.COMMENTS; User-entered notes
TAG | VARCHAR |  | Record tag (typically 'F') |  | Same as CABLES.TAG; Internal flag; observed value 'F'
INSTALL | SMALLINT |  | Installation / cable type code | 1=Pipe (Triangular), 2=LPOF, 3=Concentric Neutral, 4=Extruded, 5=Other, 6=Combined Sheath | Same as CABLES.INSTALL; Maps to InstallationType enum per CYMCAP UI
INSTSPEC | SMALLINT |  | Installation specification (currently unused) |  | Same as CABLES.INSTSPEC; All values blank in sample DB
CONDMAT | SMALLINT |  | Conductor material code | 1=Copper, 2=Aluminium | Same as CABLES.CONDMAT; Maps to ConductorMaterial enum
CONDCON | SMALLINT |  | Conductor construction code | 1-11: conductor construction code (round stranded, solid, segmental, etc.) | Same as CABLES.CONDCON; Construction type (round stranded, solid, segmental, etc.)
DRYIMPR | SMALLINT |  | Dry/impregnated insulation flag | 0,1,2,99 | Same as CABLES.DRYIMPR; Insulation paper treatment option
CONLOS | SMALLINT |  | Conductor loss calculation option | -1,0,1 | Same as CABLES.CONLOS; Controls how conductor losses are computed
INSTYP | SMALLINT |  | Insulation type code | -1=Custom, 1=Solid, 2=LPOF, 3=HPOF Self-Contained, 4=HPOF Pipe, 9=EPR, 10=PVC, 11=Polyethylene, 12=XLPE (unfilled), 13=XLPE (filled), 14=Paper | Same as CABLES.INSTYP; Maps to InsulationType enum
DIELEC | SMALLINT |  | Dielectric loss option | -3=Enter tan delta & epsilon, -1=Enter tan delta, 0=Program selects | Same as CABLES.DIELEC; Maps to DielectricOption enum
NUMCON | SMALLINT |  | Number of conductors (legacy, appears unused) | 1=Single Core, 3=Three Core | Same as CABLES.NUMCON; See NUMBCON instead
SKIDCON | SMALLINT |  | Concentric/skid wire material code | -1=Custom, 0=None, 1=Copper, 2=Brass/Bronze, 3=Zinc, 4=Stainless Steel | Same as CABLES.SKIDCON; Maps to ConcentricNeutralMaterial enum
SKNROUNDWI | SMALLINT |  | Concentric wire construction type | 1=Round Wires, 2=Flat Straps | Same as CABLES.SKNROUNDWI; Round wires vs flat straps
SHEAMAT | SMALLINT |  | Sheath material code | 0=None, 1=Aluminium, 2=Lead, 3=Lead w/ Reinforcing, 4=Copper | Same as CABLES.SHEAMAT; Maps to SheathMaterial enum
CORRUG | SMALLINT |  | Corrugation type | 1=Non-corrugated, 2=Corrugated, 3=Longitudinally Applied Tape | Same as CABLES.CORRUG; Maps to CorrugationType enum
BONDING | SMALLINT |  | Bonding configuration (currently unused) |  | Same as CABLES.BONDING; All values blank in sample DB
LOSFACT | SMALLINT |  | Loss factor override (currently unused) |  | Same as CABLES.LOSFACT; All values blank in sample DB
JACKMAT | SMALLINT |  | Jacket material code | -1=Custom, 0=None, 1=Compound Jute, 2=Rubber Sandwich, 3=Polychloroprene, 4=Polyethylene, 5=PVC, 6=EPR, 7=Butyl Rubber, 8=Coal Tar Rubber | Same as CABLES.JACKMAT; Maps to JacketMaterial enum
ARMREIN | SMALLINT |  | Armour type code | -4=Custom non-mag tape, -3=Custom mag wire/tape, -1=Custom non-mag wire, 0=None, 1=Steel wire touching, 2=Steel wire not touching, 3=Steel tape, 4=Copper wire, 5=Stainless steel wire, 6=TECK | Same as CABLES.ARMREIN; Maps to ArmourType enum
ARMBED | SMALLINT |  | Armour bedding material code | -1=Custom, 0=None, 1=Compounded Jute, 2=Rubber Sandwich | Same as CABLES.ARMBED; Maps to ArmourBedding enum
PERMEAB | SMALLINT |  | Relative permeability of armour |  | Same as CABLES.PERMEAB; Typically 0 (program default); for magnetic armour
ARMSERV | SMALLINT |  | Armour serving material code | -1=Custom, 0=None, 1=Compounded Jute | Same as CABLES.ARMSERV; Maps to ArmourServing enum
INSUSHI | SMALLINT |  | Insulation screen type | 0=No Screen, 1=Belted (unscreened), 2=Semiconductive, 3=Copper Tape, 4=Aluminium Tape | Same as CABLES.INSUSHI; Maps to InsulationScreenType enum
TAPINPIP | SMALLINT |  | Reinforcing tape over insulation screen material | 0=None, 2=Brass/Bronze, 4=Stainless Steel, 5=Steel | Same as CABLES.TAPINPIP; Material code for sheath reinforcing tape
OVERSHEATH | SMALLINT |  | Oversheath flag (currently unused) |  | Same as CABLES.OVERSHEATH; All zeros in sample DB
TRANSPO | SMALLINT |  | Transposition flag (currently unused) |  | Same as CABLES.TRANSPO; All blank in sample DB
PIPCONFI | SMALLINT |  | Pipe configuration | 0=N/A, 1=Triangular, 2=Cradled | Same as CABLES.PIPCONFI; Triangular vs cradled for pipe-type cables
PIPEMAT | SMALLINT |  | Pipe material code (currently unused) |  | Same as CABLES.PIPEMAT; Not populated in sample DB
DUCTBANK | SMALLINT |  | Duct bank reference (currently unused) |  | Same as CABLES.DUCTBANK; Not populated in sample DB
MINSECLE | SMALLINT |  | Minimum section length (currently unused) |  | Same as CABLES.MINSECLE; Not populated in sample DB
NSEGMENTS | SMALLINT |  | Number of segments for FEM meshing | 1,6 | Same as CABLES.NSEGMENTS; Conductor mesh subdivision
BRATIO | DOUBLE |  | Beta ratio (bundle conductor ratio) |  | Same as CABLES.BRATIO; Typically 1.0
SECSPAC | SMALLINT |  | Section spacing (currently unused) |  | Same as CABLES.SECSPAC; Not populated in sample DB
RHC | DOUBLE | K.m/W | Custom conductor thermal resistivity |  | Same as CABLES.RHC; Zero = program default
ALFAC | DOUBLE | 1/K | Conductor resistance temperature coefficient |  | Same as CABLES.ALFAC; Zero = program default
AKP | DOUBLE |  | Proximity effect factor kp (IEC 60287-1-1) |  | Same as CABLES.AKP; 0 = program selects; manual override for AC resistance
AKS | DOUBLE |  | Skin effect factor ks (IEC 60287-1-1) |  | Same as CABLES.AKS; 0 = program selects; 0.001 stored when GUI shows 0.0
RHI | DOUBLE | K.m/W | Custom insulation thermal resistivity |  | Same as CABLES.RHI; Used when INSTYP=-1 (custom)
COSPHI | DOUBLE |  | Insulation dielectric loss tangent (tan delta) |  | Same as CABLES.COSPHI; Custom value used when DIELEC=-1 or -3
EPSILN | DOUBLE |  | Insulation relative permittivity (epsilon_r) |  | Same as CABLES.EPSILN; Custom value used when DIELEC=-3
RHK | DOUBLE | ohm.m | Custom concentric neutral wire electrical resistivity |  | Same as CABLES.RHK; Used when SKIDCON=-1 (custom)
ALFAK | DOUBLE | 1/K | Concentric neutral resistance temperature coefficient |  | Same as CABLES.ALFAK; Per K at 20°C
RHS | DOUBLE | ohm.m | Custom sheath electrical resistivity |  | Same as CABLES.RHS; Zero = program default for selected material
ALFAS | DOUBLE | 1/K | Sheath resistance temperature coefficient |  | Same as CABLES.ALFAS; Zero = program default
ALOS | DOUBLE |  | Additional losses factor (currently unused) |  | Same as CABLES.ALOS; All blank in sample DB
RHJ | DOUBLE | K.m/W | Custom jacket thermal resistivity |  | Same as CABLES.RHJ; Used when JACKMAT=-1 (custom)
RHA | DOUBLE | ohm.m | Custom armour electrical resistivity at 20°C |  | Same as CABLES.RHA; Value in Ω·m (e.g. 1.38e-7)
ALFAA | DOUBLE | 1/K | Armour resistance temperature coefficient at 20°C |  | Same as CABLES.ALFAA; Per K
RHB | DOUBLE | K.m/W | Armour bedding thermal resistivity |  | Same as CABLES.RHB; Used when ARMBED=-1 (custom)
AME | DOUBLE |  | Unknown material parameter (always 0) |  | Same as CABLES.AME; Currently zero for everything
AMT | DOUBLE |  | Unknown material parameter (always 0) |  | Same as CABLES.AMT; Currently zero for everything
GAMMA | DOUBLE |  | Unknown material parameter (always 0) |  | Same as CABLES.GAMMA; Currently zero for everything
RHAS | DOUBLE | K.m/W | Armour serving thermal resistivity |  | Same as CABLES.RHAS; Used when ARMSERV=-1 (custom)
RHT | DOUBLE | K.m/W | Unknown thermal resistivity (always 0) |  | Same as CABLES.RHT; Currently zero for everything
ALFAT | DOUBLE | 1/K | Unknown temperature coefficient (always 0) |  | Same as CABLES.ALFAT; Currently zero for everything
RHO | DOUBLE |  | Unknown resistivity parameter (always 0) |  | Same as CABLES.RHO; Currently zero for everything
PIPFAC | DOUBLE |  | Pipe factor (currently unused) |  | Same as CABLES.PIPFAC; All blank in sample DB
AM | DOUBLE |  | Unknown parameter (currently unused) |  | Same as CABLES.AM; All blank in sample DB
AN | DOUBLE |  | Unknown parameter (currently unused) |  | Same as CABLES.AN; All blank in sample DB
NSECT | SMALLINT |  | Number of sections (currently unused) |  | Same as CABLES.NSECT; All blank in sample DB
RHD | DOUBLE |  | Unknown thermal resistivity (currently unused) |  | Same as CABLES.RHD; All blank in sample DB
NUMBCON | SMALLINT |  | Number of cores/conductors | 1=Single Core, 3=Three Core | Same as CABLES.NUMBCON; 1=Single Core, 3=Three Core
CONAREA | DOUBLE | m² | Conductor cross-sectional area |  | Same as CABLES.CONAREA; Standard cable conductor area in m²
CONDIAM | DOUBLE | m | Conductor outer diameter |  | Same as CABLES.CONDIAM; Diameter in metres
CONSHDI | DOUBLE | m | Diameter over conductor shield |  | Same as CABLES.CONSHDI; Outer diameter after conductor shield layer
CONSPAC | DOUBLE | m | Three-core cable conductor spacing diameter |  | Same as CABLES.CONSPAC; Diameter after individual cores in 3-core cable
CONINDI | DOUBLE | m | Conductor inner diameter (hollow core) |  | Same as CABLES.CONINDI; For hollow-core/oil-channel conductors
CONEQDI | DOUBLE | m | Conductor equivalent diameter |  | Same as CABLES.CONEQDI; Used for sector-shaped conductors
CENTRDIS | DOUBLE | m | Centre distance between conductors |  | Same as CABLES.CENTRDIS; Only populated for specific cable types
RADCIRC | DOUBLE | m | Radius of circle through 3-core conductors |  | Same as CABLES.RADCIRC; For 3-core sector-shaped cables
VOLTAGE | DOUBLE | V | Rated voltage |  | Same as CABLES.VOLTAGE; Phase-to-ground voltage in Volts
INSUDIA | DOUBLE | m | Insulation outer diameter |  | Same as CABLES.INSUDIA; Diameter over insulation in metres
INSHIDI | DOUBLE | m | Insulation inner (shield) diameter |  | Same as CABLES.INSHIDI; Inner diameter of insulation screen layer
INSTHIC | DOUBLE | m | Insulation thickness |  | Same as CABLES.INSTHIC; For 3-core: 2× insulation thickness
CINSSHTH | DOUBLE | m | Common insulation screen thickness (3-core) |  | Same as CABLES.CINSSHTH; 2× insulation screen thickness for 3-core cables
INSSHTH | DOUBLE | m | Insulation screen thickness (individual) |  | Same as CABLES.INSSHTH; Per-core insulation screen thickness
MESHITH | DOUBLE | m | Metallic insulation screen thickness |  | Same as CABLES.MESHITH; Thickness of metallic insulation screen
CIRCIRDI | DOUBLE | m | Unknown diameter (rare usage) |  | Same as CABLES.CIRCIRDI; Only populated in one cable (case 51)
SHEATHDI | DOUBLE | m | Sheath outer diameter |  | Same as CABLES.SHEATHDI; Metallic sheath outer diameter in metres
SHETHIC | DOUBLE | m | Sheath thickness |  | Same as CABLES.SHETHIC; Metallic sheath thickness in metres
SHINRAD | DOUBLE | m | Corrugated sheath inner radius |  | Same as CABLES.SHINRAD; Inner trough radius for corrugated sheaths
SHOUTRAD | DOUBLE | m | Corrugated sheath outer radius |  | Same as CABLES.SHOUTRAD; Outer crest radius for corrugated sheaths
TAPBIND | DOUBLE | m | Tape over insulation screen — outer diameter |  | Same as CABLES.TAPBIND; Diameter after tape application
TAPBINTH | DOUBLE | m | Tape over insulation screen — thickness |  | Same as CABLES.TAPBINTH; Tape thickness in metres
TAPBINWI | DOUBLE | m | Tape over insulation screen — width |  | Same as CABLES.TAPBINWI; Tape width in metres
TAPENUM | SMALLINT |  | Number of tapes over insulation screen |  | Same as CABLES.TAPENUM; Integer count
LAYLENG | DOUBLE | m | Tape lay length |  | Same as CABLES.LAYLENG; Helical lay length of tape
LAYLENG1 | DOUBLE | m | Tape lay length (secondary, unclear usage) |  | Same as CABLES.LAYLENG1; Purpose unclear
OVSHETDI | DOUBLE | m | Armour bedding outer diameter |  | Same as CABLES.OVSHETDI; Diameter after armour bedding; rarely populated
OVSHETH | DOUBLE | m | Armour bedding thickness (alternative) |  | Same as CABLES.OVSHETH; Rarely populated
JACKDIA | DOUBLE | m | Jacket outer diameter |  | Same as CABLES.JACKDIA; Non-metallic jacket outer diameter
JACKTHI | DOUBLE | m | Jacket thickness |  | Same as CABLES.JACKTHI; Non-metallic jacket thickness
ARMBEDTH | DOUBLE | m | Armour bedding thickness |  | Same as CABLES.ARMBEDTH; Bedding layer thickness in metres
ARMSERTH | DOUBLE | m | Armour serving thickness |  | Same as CABLES.ARMSERTH; Serving layer thickness in metres
SKINEUDI | DOUBLE | m | Diameter over concentric neutral wires |  | Same as CABLES.SKINEUDI; Outer diameter after concentric wire layer
SKNSTRAPLG | DOUBLE | m | Concentric neutral strap width |  | Same as CABLES.SKNSTRAPLG; Width of flat strap (when flat straps selected)
WIARMDIA | DOUBLE | m | Diameter over wire armour |  | Same as CABLES.WIARMDIA; Outer diameter after armour wire layer
TAPARMDI | DOUBLE | m | Diameter over tape armour |  | Same as CABLES.TAPARMDI; Outer diameter after armour tape layer
SKNEWIDI | DOUBLE | m | Concentric neutral wire diameter |  | Same as CABLES.SKNEWIDI; Individual wire diameter
ARMWIRDI | DOUBLE | m | Armour wire diameter |  | Same as CABLES.ARMWIRDI; Individual armour wire diameter
TAPARMAR | DOUBLE | m² | Armour tape cross-sectional area |  | Same as CABLES.TAPARMAR; For tape armour where width not separately defined
SKNEWILE | DOUBLE | m | Concentric neutral wire lay length |  | Same as CABLES.SKNEWILE; Helical lay length
ARMWIRLE | DOUBLE | m | Armour wire lay length |  | Same as CABLES.ARMWIRLE; Helical lay length
SKNEWINU | SMALLINT |  | Number of concentric neutral wires |  | Same as CABLES.SKNEWINU; Integer count
ARMWIRNU | SMALLINT |  | Number of armour wires |  | Same as CABLES.ARMWIRNU; Integer count
OVERDIAM | DOUBLE | m | Overall cable outer diameter |  | Same as CABLES.OVERDIAM; Final outer diameter of complete cable
DUPIINDI | DOUBLE | m | Duct/pipe inner diameter (currently unused) |  | Same as CABLES.DUPIINDI; Not populated in sample DB
DUPIOTDI | DOUBLE | m | Duct/pipe outer diameter (currently unused) |  | Same as CABLES.DUPIOTDI; Not populated in sample DB
SLCSHTH | SMALLINT |  | Sheath configuration for 3-core cables | 1=Individual, 2=Common | Same as CABLES.SLCSHTH; Whether sheath is per-core or common
SLCCONC | SMALLINT |  | Concentric wire configuration for 3-core cables | 1=Individual, 2=Common | Same as CABLES.SLCCONC; Whether concentric wires are per-core or common
CORRUGHGT | DOUBLE | m | Corrugation height |  | Same as CABLES.CORRUGHGT; Height of corrugation on corrugated sheath
TAPOVERLAP | DOUBLE | m | Tape overlap |  | Same as CABLES.TAPOVERLAP; Overlap distance for helically applied tapes
TAPWIDTH | DOUBLE | m | Tape width |  | Same as CABLES.TAPWIDTH; Width of reinforcing/screen tape
TAPTH | DOUBLE | m | Tape thickness |  | Same as CABLES.TAPTH; Thickness of reinforcing/screen tape
ACCFACTOR | DOUBLE |  | Accumulation factor |  | Same as CABLES.ACCFACTOR; Purpose unclear; possibly for bundled cables
DCRESIS | DOUBLE | ohm/m | DC resistance at 20°C |  | Same as CABLES.DCRESIS; Conductor DC resistance per metre
DOVLCSHLD | DOUBLE | m | Diameter over longitudinal cable shield |  | Same as CABLES.DOVLCSHLD; Only for longitudinally applied tapes
CONDCNAM | VARCHAR |  | Custom conductor material name |  | Same as CABLES.CONDCNAM; Text label for custom conductor
INSUCNAM | VARCHAR |  | Custom insulation material name |  | Same as CABLES.INSUCNAM; Text label for custom insulation
SHTHCNAM | VARCHAR |  | Custom sheath material name |  | Same as CABLES.SHTHCNAM; Text label for custom sheath
REINFCNAM | VARCHAR |  | Custom reinforcing tape material name |  | Same as CABLES.REINFCNAM; Text label for custom reinforcing
SKIDCNAM | VARCHAR |  | Custom concentric/skid wire material name |  | Same as CABLES.SKIDCNAM; Text label for custom wire material
OVSHTHCNAM | VARCHAR |  | Custom oversheath material name |  | Same as CABLES.OVSHTHCNAM; Text label
ARMBEDCNAM | VARCHAR |  | Custom armour bedding material name |  | Same as CABLES.ARMBEDCNAM; Text label
ARMOURCNAM | VARCHAR |  | Custom armour material name |  | Same as CABLES.ARMOURCNAM; Text label
ARMSRVCNAM | VARCHAR |  | Custom armour serving material name |  | Same as CABLES.ARMSRVCNAM; Text label
JACKETCNAM | VARCHAR |  | Custom jacket material name |  | Same as CABLES.JACKETCNAM; Text label
SS_TEMP | SMALLINT | °C | Maximum steady-state conductor temperature |  | Same as CABLES.SS_TEMP; IEC 60287 maximum operating temperature
TR_TEMP | SMALLINT | °C | Maximum transient/emergency conductor temperature |  | Same as CABLES.TR_TEMP; IEC 60853 emergency rating temperature
MSTR_IDCAB | VARCHAR |  | Master cable ID reference (currently unused) |  | Same as CABLES.MSTR_IDCAB; Not populated in sample DB
ShCctConductorData | VARCHAR |  | Short-circuit conductor data (CSV string) |  | Same as CABLES.ShCctConductorData; Format: rho,alpha,maxT,duration,flag
ShCctSheathData | VARCHAR |  | Short-circuit sheath data (CSV string) |  | Same as CABLES.ShCctSheathData; Format: rho,alpha,maxT,duration,flag
ShCctReinforcingTapeData | VARCHAR |  | Short-circuit reinforcing tape data (CSV string) |  | Same as CABLES.ShCctReinforcingTapeData; Format: rho,alpha,maxT,duration,flag
ShCctSkidConcentricData | VARCHAR |  | Short-circuit concentric/skid data (CSV string) |  | Same as CABLES.ShCctSkidConcentricData; Format: rho,alpha,maxT,duration,flag
ShCctArmourData | VARCHAR |  | Short-circuit armour data (CSV string) |  | Same as CABLES.ShCctArmourData; Format: rho,alpha,maxT,duration,flag
ShCctPipeCoatingMaterial | INTEGER |  | Short-circuit pipe coating material |  | Same as CABLES.ShCctPipeCoatingMaterial; Not populated
ShCctPipeCoatingCustomRHJ | DOUBLE | K.m/W | Custom pipe coating thermal resistivity |  | Same as CABLES.ShCctPipeCoatingCustomRHJ; Not populated
ShCctPipeMaterial | INTEGER |  | Short-circuit pipe material code |  | Same as CABLES.ShCctPipeMaterial; Not populated
ShCctPipeFactor | DOUBLE |  | Short-circuit pipe factor |  | Same as CABLES.ShCctPipeFactor; Not populated
ShCctInsideDuctDiam | DOUBLE | m | Short-circuit inside duct diameter |  | Same as CABLES.ShCctInsideDuctDiam; Not populated
ShCctOutsideDuctDiam | DOUBLE | m | Short-circuit outside duct diameter |  | Same as CABLES.ShCctOutsideDuctDiam; Not populated
ShCctOverallDuctDiam | DOUBLE | m | Short-circuit overall duct diameter |  | Same as CABLES.ShCctOverallDuctDiam; Not populated
FillersSameAsInsuFlag | INTEGER |  | Filler material same-as-insulation flag | -99=No Fillers, 0=Custom, 1=Same as insulation | Same as CABLES.FillersSameAsInsuFlag; For 3-core cable fillers
FillersResis | DOUBLE | K.m/W | Filler thermal resistivity |  | Same as CABLES.FillersResis; Custom filler thermal resistivity
NbrOfWiresComposingStrandedConductor | INTEGER |  | Number of strands in conductor |  | Same as CABLES.NbrOfWiresComposingStrandedConductor; Used for inductance calculations
WireGauge | INTEGER |  | Wire gauge selection code |  | Same as CABLES.WireGauge; Concentric wire gauge; affects thickness/diameter
CasingInsideDiam | DOUBLE | m | Casing inside diameter (unused) |  | Same as CABLES.CasingInsideDiam; Not populated
CasingOutsideDiam | DOUBLE | m | Casing outside diameter (unused) |  | Same as CABLES.CasingOutsideDiam; Not populated
CasingConst | INTEGER |  | Casing construction code (unused) |  | Same as CABLES.CasingConst; Not populated
CasingRh | DOUBLE | K.m/W | Casing thermal resistivity (unused) |  | Same as CABLES.CasingRh; Not populated
CasingFormation | INTEGER |  | Casing formation code (unused) |  | Same as CABLES.CasingFormation; Not populated
ArmourEmbeddedPEInnerTh | DOUBLE | m | PE/AL/PE armour — inner PE thickness |  | Same as CABLES.ArmourEmbeddedPEInnerTh; For PE/AL/PE laminate armour
ArmourEmbeddedAluminumTh | DOUBLE | m | PE/AL/PE armour — aluminium thickness |  | Same as CABLES.ArmourEmbeddedAluminumTh; For PE/AL/PE laminate armour
ArmourEmbeddedPEOuterTh | DOUBLE | m | PE/AL/PE armour — outer PE thickness |  | Same as CABLES.ArmourEmbeddedPEOuterTh; For PE/AL/PE laminate armour
PrintingCompactCompressedFlag | INTEGER |  | Compact vs compressed conductor label flag | 0=Compressed, 1=Compact | Same as CABLES.PrintingCompactCompressedFlag; Display label only
SideBySidePictFileName | VARCHAR |  | Side-by-side picture filename (GUI) |  | Same as CABLES.SideBySidePictFileName; GUI display field
SideBySidePictScaleIndex | INTEGER |  | Picture scale index (GUI) |  | Same as CABLES.SideBySidePictScaleIndex; GUI display field
DataSheetFileNames | LONGCHAR |  | Attached data sheet filenames (GUI) |  | Same as CABLES.DataSheetFileNames; GUI display field
CrossBondedTransposition | INTEGER |  | Cross-bonded transposition configuration |  | Bonding arrangement for study cable
GMRConductor | DOUBLE | m | Geometric mean radius — conductor |  | Same as CABLES.GMRConductor; For impedance calculations
GMRSheath | DOUBLE | m | Geometric mean radius — sheath |  | Same as CABLES.GMRSheath; For impedance calculations
GMRConcentricNeutral | DOUBLE | m | Geometric mean radius — concentric neutral |  | Same as CABLES.GMRConcentricNeutral; For impedance calculations
LongestSection | DOUBLE | m | Longest bonding section length |  | Same as CABLES.LongestSection; For cross-bonding calculations
LongerSection | DOUBLE | m | Longer bonding section length |  | Same as CABLES.LongerSection; For cross-bonding calculations
ShortestSection | DOUBLE | m | Shortest bonding section length |  | Same as CABLES.ShortestSection; For cross-bonding calculations
BETAC | DOUBLE | J/(m³·K) | Conductor volumetric thermal capacitance |  | Same as CABLES.BETAC; IEC 60853 transient parameter
SHC | DOUBLE | J/(kg·K) | Conductor specific heat capacity |  | Same as CABLES.SHC; IEC 60853 transient parameter
BETAS | DOUBLE | J/(m³·K) | Sheath volumetric thermal capacitance |  | Same as CABLES.BETAS; IEC 60853 transient parameter
SHS | DOUBLE | J/(kg·K) | Sheath specific heat capacity |  | Same as CABLES.SHS; IEC 60853 transient parameter
BETAT | DOUBLE | J/(m³·K) | Reinforcing tape volumetric thermal capacitance |  | Same as CABLES.BETAT; IEC 60853 transient parameter
SHT | DOUBLE | J/(kg·K) | Reinforcing tape specific heat capacity |  | Same as CABLES.SHT; IEC 60853 transient parameter
BETAK | DOUBLE | J/(m³·K) | Concentric neutral volumetric thermal capacitance |  | Same as CABLES.BETAK; IEC 60853 transient parameter
SHK | DOUBLE | J/(kg·K) | Concentric neutral specific heat capacity |  | Same as CABLES.SHK; IEC 60853 transient parameter
BETAA | DOUBLE | J/(m³·K) | Armour volumetric thermal capacitance |  | Same as CABLES.BETAA; IEC 60853 transient parameter
SHA | DOUBLE | J/(kg·K) | Armour specific heat capacity |  | Same as CABLES.SHA; IEC 60853 transient parameter
Dimension_correction_flag | INTEGER |  | Dimension correction flag | 0,2 | Same as CABLES.Dimension_correction_flag; Purpose unclear
Duct_custom_U | DOUBLE |  | Custom duct parameter U (unused) |  | Same as CABLES.Duct_custom_U; Not populated
Duct_custom_V | DOUBLE |  | Custom duct parameter V (unused) |  | Same as CABLES.Duct_custom_V; Not populated
Duct_custom_Y | DOUBLE |  | Custom duct parameter Y (unused) |  | Same as CABLES.Duct_custom_Y; Not populated
JACKETMAT_SLTYPE | INTEGER |  | Per-core jacket material code (3-core) | -1=Custom, 0=None, 1=Compound Jute, 2=Rubber Sandwich, 3=Polychloroprene, 4=Polyethylene, 5=PVC, 6=EPR, 7=Butyl Rubber, 8=Coal Tar Rubber | Same as CABLES.JACKETMAT_SLTYPE; Jacket around each individual core
JACKETCNAM_SLTYPE | VARCHAR |  | Per-core custom jacket material name |  | Same as CABLES.JACKETCNAM_SLTYPE; Text label
RHJ_SLTYPE | DOUBLE | K.m/W | Per-core custom jacket thermal resistivity |  | Same as CABLES.RHJ_SLTYPE; For individual core jackets
JACKET_THI_SLTYPE | DOUBLE | m | Per-core jacket thickness |  | Same as CABLES.JACKET_THI_SLTYPE; Only for specific cable types (e.g. city cable)
GROUP_CABLE_NAME | VARCHAR |  | Cable group/folder name |  | Same as CABLES.GROUP_CABLE_NAME; Organizational folder in CYMCAP UI
K_SpecificInsulationResis | DOUBLE | M.ohm.km | K factor for insulation resistance |  | Same as CABLES.K_SpecificInsulationResis; Specific insulation resistance
Frequency_flag | INTEGER |  | Frequency calculation flag (unused) |  | Same as CABLES.Frequency_flag; Not populated
Frequency | DOUBLE | Hz | System frequency (cable-level override) |  | Same as CABLES.Frequency; Not populated; typically set at study level
INSSYS | INTEGER |  | Insulation system code | 1,2 | Same as CABLES.INSSYS; Purpose unclear
MILWIRECON | INTEGER |  | Milliken wire construction type | 1=Insulated, 2=Unidirectional, 3=Bidirectional | Same as CABLES.MILWIRECON; For Milliken conductors
MEDIUM_DUCT_FLAG | INTEGER |  | Medium/duct flag (unused) |  | Same as CABLES.MEDIUM_DUCT_FLAG; Not populated
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property flag (unused) |  | Same as CABLES.MAGNETIC_PROPERTY_FLAG; Not populated
DUCT_FILLING_TH_RESIS | DOUBLE | K.m/W | Duct filling thermal resistivity |  | Thermal resistivity of duct fill material
OUTER_CABLE_PHASE_FLAG | INTEGER |  | Outer cable phase flag (unused) |  | Same as CABLES.OUTER_CABLE_PHASE_FLAG; Not populated
CONDSHLDMAT | INTEGER |  | Conductor shield material code | -1=Custom, 0=Same as insulation, 15=Semiconductive, 99=Undefined | Same as CABLES.CONDSHLDMAT; Maps to ConductorShieldMaterial enum
RHCS | DOUBLE | K.m/W | Custom conductor shield thermal resistivity |  | Same as CABLES.RHCS; Used when CONDSHLDMAT=-1 (custom)
CONDSHLDCNAM | CHAR |  | Custom conductor shield material name |  | Same as CABLES.CONDSHLDCNAM; Text label
CORE_LENGTH_OF_LAY | DOUBLE | m | Core length of lay (3-core cables) |  | Same as CABLES.CORE_LENGTH_OF_LAY; Helical lay length of individual cores
LENGTH_OF_PITCH | DOUBLE | m | Corrugated sheath pitch length |  | Same as CABLES.LENGTH_OF_PITCH; Corrugation pitch for corrugated sheaths
ARMROUNDWI | INTEGER |  | Armour wire shape flag | 0=N/A, 1=Round Wire, 2=Flat Straps | Same as CABLES.ARMROUNDWI; Wire vs strap armour
ARMSTRAPLG | DOUBLE | m | Armour strap width |  | Same as CABLES.ARMSTRAPLG; Width of flat strap armour
ACDC_FLAG | INTEGER |  | AC/DC flag | 0=AC, 1=DC | Same as CABLES.ACDC_FLAG; Maps to AcDcFlag enum
ARMREIN2 | INTEGER |  | Second armour type code (second armour layer — not populated) |  | Same as CABLES.ARMREIN2; For double-armoured cables; not used in sample DB
ARMBED2 | INTEGER |  | Second armour bedding material (second armour layer — not populated) |  | Same as CABLES.ARMBED2; For double-armoured cables; not used in sample DB
ARMBEDTH2 | DOUBLE |  | Second armour bedding thickness (second armour layer — not populated) |  | Same as CABLES.ARMBEDTH2; For double-armoured cables; not used in sample DB
ARMBED_DIAM2 | DOUBLE |  | Second armour bedding diameter (second armour layer — not populated) |  | Same as CABLES.ARMBED_DIAM2; For double-armoured cables; not used in sample DB
ARMWIRDI2 | DOUBLE |  | Second armour wire diameter (second armour layer — not populated) |  | Same as CABLES.ARMWIRDI2; For double-armoured cables; not used in sample DB
WIARMDIA2 | DOUBLE |  | Second armour outer diameter (second armour layer — not populated) |  | Same as CABLES.WIARMDIA2; For double-armoured cables; not used in sample DB
TAPARMAR2 | DOUBLE |  | Second armour tape area (second armour layer — not populated) |  | Same as CABLES.TAPARMAR2; For double-armoured cables; not used in sample DB
ARMWIRLE2 | DOUBLE |  | Second armour wire lay length (second armour layer — not populated) |  | Same as CABLES.ARMWIRLE2; For double-armoured cables; not used in sample DB
TAPARMDI2 | DOUBLE |  | Second armour tape diameter (second armour layer — not populated) |  | Same as CABLES.TAPARMDI2; For double-armoured cables; not used in sample DB
ARMWIRNU2 | INTEGER |  | Second armour wire count (second armour layer — not populated) |  | Same as CABLES.ARMWIRNU2; For double-armoured cables; not used in sample DB
ARMROUNDWI2 | INTEGER |  | Second armour wire shape (second armour layer — not populated) |  | Same as CABLES.ARMROUNDWI2; For double-armoured cables; not used in sample DB
ARMSTRAPLG2 | DOUBLE |  | Second armour strap width (second armour layer — not populated) |  | Same as CABLES.ARMSTRAPLG2; For double-armoured cables; not used in sample DB
ArmourEmbeddedPEInnerTh2 | DOUBLE |  | Second armour PE inner thickness (second armour layer — not populated) |  | Same as CABLES.ArmourEmbeddedPEInnerTh2; For double-armoured cables; not used in sample DB
ArmourEmbeddedAluminumTh2 | DOUBLE |  | Second armour aluminium thickness (second armour layer — not populated) |  | Same as CABLES.ArmourEmbeddedAluminumTh2; For double-armoured cables; not used in sample DB
ArmourEmbeddedPEOuterTh2 | DOUBLE |  | Second armour PE outer thickness (second armour layer — not populated) |  | Same as CABLES.ArmourEmbeddedPEOuterTh2; For double-armoured cables; not used in sample DB
PERMEAB2 | INTEGER |  | Second armour permeability (second armour layer — not populated) |  | Same as CABLES.PERMEAB2; For double-armoured cables; not used in sample DB
RHA2 | DOUBLE |  | Second armour resistivity (second armour layer — not populated) |  | Same as CABLES.RHA2; For double-armoured cables; not used in sample DB
ALFAA2 | DOUBLE |  | Second armour temp coefficient (second armour layer — not populated) |  | Same as CABLES.ALFAA2; For double-armoured cables; not used in sample DB
BETAA2 | DOUBLE |  | Second armour thermal capacitance (second armour layer — not populated) |  | Same as CABLES.BETAA2; For double-armoured cables; not used in sample DB
SHA2 | DOUBLE |  | Second armour specific heat (second armour layer — not populated) |  | Same as CABLES.SHA2; For double-armoured cables; not used in sample DB
RHB2 | DOUBLE |  | Second armour bedding thermal resistivity (second armour layer — not populated) |  | Same as CABLES.RHB2; For double-armoured cables; not used in sample DB
AME2 | DOUBLE |  | Second armour AME parameter (second armour layer — not populated) |  | Same as CABLES.AME2; For double-armoured cables; not used in sample DB
AMT2 | DOUBLE |  | Second armour AMT parameter (second armour layer — not populated) |  | Same as CABLES.AMT2; For double-armoured cables; not used in sample DB
GAMMA2 | DOUBLE |  | Second armour GAMMA parameter (second armour layer — not populated) |  | Same as CABLES.GAMMA2; For double-armoured cables; not used in sample DB
ARMBEDCNAM2 | CHAR |  | Second armour bedding custom material name (second armour layer — not populated) |  | Same as CABLES.ARMBEDCNAM2; For double-armoured cables; not used in sample DB
ARMOURCNAM2 | CHAR |  | Second armour custom material name (second armour layer — not populated) |  | Same as CABLES.ARMOURCNAM2; For double-armoured cables; not used in sample DB
CITYCABLE_FLAG | INTEGER |  | Retrofitted city cable flag | 1=City cable (e.g. CIGRE Case 9) | Same as CABLES.CITYCABLE_FLAG; Indicates special city cable configuration
ShCctSecondArmourData | CHAR |  | Short-circuit second armour data (CSV string) |  | Same as CABLES.ShCctSecondArmourData; For double-armoured cables

## MULTIPLELAYER
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | DOUBLE |  | Execution number |  | Sub-case identifier
TAG | VARCHAR |  | Record tag |  | Internal flag
LAYERNO | SMALLINT |  | Layer number (0-based) |  | Index of this soil/backfill layer
LAYERTYPE | INTEGER |  | Layer type |  | Soil, backfill, duct bank, etc.
LAYERNAME | VARCHAR |  | Layer display name |  | User-entered label
LAYERCAPTION | VARCHAR |  | Layer caption (GUI) |  | GUI display label
XLEFT | DOUBLE | m | Left edge X coordinate |  | Layer boundary
YTOP | DOUBLE | m | Top edge Y coordinate (depth) |  | Layer boundary
XB | DOUBLE | m | Layer width |  | Horizontal extent
YB | DOUBLE | m | Layer height |  | Vertical extent
AXB | DOUBLE |  | Drawing axis parameter (GUI) |  | Cross-section display
AYB | DOUBLE |  | Drawing Y-axis parameter (GUI) |  | Cross-section display
DUCTYPOS | SMALLINT | m | Duct bank Y position within layer |  | Depth of duct bank
DUCTBANKID | VARCHAR |  | Duct bank library ID |  | FK to DUCTLIB
DUCTBANK | SMALLINT |  | Duct bank name |  | Display name
RHD | DOUBLE | K.m/W | Duct thermal resistivity |  | Duct material property
ALIGN_HOR | SMALLINT |  | Horizontal alignment (GUI) |  | GUI display
ALIGN_VER | SMALLINT |  | Vertical alignment (GUI) |  | GUI display
LAYERCOLOR | SMALLINT |  | Layer colour code (GUI) |  | GUI display
LAYERRESIS | DOUBLE | K.m/W | Layer thermal resistivity |  | Soil/backfill thermal resistivity
INSIDE_DIAM | DOUBLE | m | Casing inside diameter |  | For casing within layer
OUTSIDE_DIAM | DOUBLE | m | Casing outside diameter |  | For casing within layer
CASING_CONFIGURATION_TYPE | INTEGER |  | Casing configuration type |  | Casing arrangement
CASING_CONSTRUCTION_TYPE | INTEGER |  | Casing construction type |  | Casing material/build
DUCT_ATTACHED_TO_CASING_INDEX | INTEGER |  | Index of duct attached to casing |  | Casing-duct linkage
SHAPETYPE | INTEGER |  | Layer shape type |  | Cross-section shape (rectangular, trapezoidal, etc.)
FRAME_XCENTRE | DOUBLE | m | Frame X centre (GUI) |  | GUI frame position
FRAME_YCENTRE | DOUBLE | m | Frame Y centre (GUI) |  | GUI frame position
FRAME_XLEFT | DOUBLE | m | Frame left edge (GUI) |  | GUI frame position
FRAME_YTOP | DOUBLE | m | Frame top edge (GUI) |  | GUI frame position
FRAME_WIDTH | DOUBLE | m | Frame width (GUI) |  | GUI frame size
FRAME_HEIGHT | DOUBLE | m | Frame height (GUI) |  | GUI frame size
FRAME_LAYERCOLOR | INTEGER |  | Frame layer colour (GUI) |  | GUI display
FRAME_LAYERRESIS | INTEGER | K.m/W | Frame layer thermal resistivity |  | Encasement material property
DUCTXPOS | INTEGER | m | Duct X position within layer |  | Horizontal position of duct
LAYER_RESIS_SAME_AS_SOIL_RESIS_FLAG | INTEGER |  | Layer resistivity same as soil flag |  | Whether layer inherits soil properties
DUCT_CUSTOM_U | DOUBLE |  | Custom duct thermal parameter U |  | Custom thermal coefficient
DUCT_CUSTOM_V | DOUBLE |  | Custom duct thermal parameter V |  | Custom thermal coefficient
DUCT_CUSTOM_Y | DOUBLE |  | Custom duct thermal parameter Y |  | Custom thermal coefficient
LD_ARROW_WIDTH_POSITION | INTEGER |  | Layer dimension arrow width position (GUI) |  | GUI dimension display
LD_ARROW_WIDTH_MARGIN | DOUBLE |  | Layer dimension arrow width margin (GUI) |  | GUI dimension display
LD_ARROW_WIDTH_INSIDECOMPO_FLAG | INTEGER |  | Width arrow inside component flag (GUI) |  | GUI dimension display
LD_ARROW_HEIGHT_POSITION | INTEGER |  | Layer dimension arrow height position (GUI) |  | GUI dimension display
LD_ARROW_HEIGHT_MARGIN | DOUBLE |  | Layer dimension arrow height margin (GUI) |  | GUI dimension display
LD_ARROW_HEIGHT_INSIDECOMPO_FLAG | INTEGER |  | Height arrow inside component flag (GUI) |  | GUI dimension display
MEDIUM_DUCT_FLAG | INTEGER |  | Medium duct flag |  | Duct fill medium type
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property flag |  | Include magnetic effects
FRAME_LAYERRESIS_NEW | DOUBLE | K.m/W | Updated frame layer thermal resistivity |  | Updated encasement property
REAL_DUCTS_IN_TREFOIL_YCENTRE | DOUBLE | m | Real duct trefoil Y centre |  | Actual trefoil position
DUCT_FILLING_TH_RESIS | DOUBLE | K.m/W | Duct filling thermal resistivity |  | Thermal resistivity of duct fill material
DUCT_IN_TREFOIL_RECALCULATED_FLAG | INTEGER |  | Duct trefoil recalculated flag |  | Whether trefoil positions were recalculated

## CALCTYPE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | SMALLINT |  | Execution number |  | Sub-case identifier
TAG | VARCHAR |  | Record tag |  | Internal flag

## STUDYHED
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — unique identifier |  | Primary key, VARCHAR
EXECUNO | SMALLINT |  | Execution number within study |  | Sub-case identifier within study
STUDYTITLE | VARCHAR |  | Study title |  | User-entered study description
EXECDATE | VARCHAR |  | Execution date |  | Date of calculation run
COMMENTS | VARCHAR |  | Study comments |  | User-entered notes
EXECUTITLE | VARCHAR |  | Execution title |  | User-entered sub-case description
TAG | VARCHAR |  | Record tag |  | Internal flag
TAG2 | VARCHAR |  | Secondary record tag |  | Internal flag
MODECALC | SMALLINT |  | Calculation mode | Calculation mode code | Which calculation method to use
NCABLE | SMALLINT |  | Number of cables in study |  | Count of cable positions
NTYPE | SMALLINT |  | Number of cable types |  | Distinct cable designs used
AMBIENT | DOUBLE | °C | Ambient soil/air temperature |  | IEC 60287 ambient temperature
RHOS | DOUBLE | K.m/W | Native soil thermal resistivity |  | IEC 60287 soil thermal resistivity
IREFCA | SMALLINT | A | Reference cable current |  | Initial/reference current for iteration
XB | DOUBLE | m | Drawing X boundary (GUI) |  | Cross-section view boundary
YB | DOUBLE | m | Drawing Y boundary (GUI) |  | Cross-section view boundary
ALB | DOUBLE |  | Drawing scale parameter (GUI) |  | Cross-section view scale
AXB | DOUBLE |  | Drawing axis parameter (GUI) |  | Cross-section view axis
RHOB | DOUBLE | K.m/W | Backfill thermal resistivity |  | Thermal resistivity of installed backfill
CABINAIR | VARCHAR |  | Cable in air flag |  | Whether any cables are in air
EXTHEAT | VARCHAR | W/m | External heat source rate |  | External heat dissipation per unit length
TEMTOL | DOUBLE | °C | Temperature convergence tolerance |  | Solver convergence criterion
AMPTOL | DOUBLE | A | Ampacity convergence tolerance |  | Solver convergence criterion
MAXNIT | SMALLINT |  | Maximum iterations |  | Solver iteration limit
TRTOL | DOUBLE |  | Transient tolerance |  | Transient solver convergence criterion
TRSTEP | DOUBLE | s | Transient time step |  | Transient solver time step
TRMAXNIT | SMALLINT |  | Transient max iterations |  | Transient solver iteration limit
FRACT | DOUBLE |  | Load fraction |  | Fraction of full load for calculation
FREQ | DOUBLE | Hz | System frequency |  | 50 or 60 Hz for AC loss calculations
PRINTI | SMALLINT |  | Print intermediate results flag |  | Output control
PRINT | SMALLINT |  | Print results flag |  | Output control
EXRESMO | SMALLINT |  | Extended results mode |  | Output detail level
CAAIRAR | SMALLINT |  | Cable in air arrangement |  | Configuration for cables in air
SHADED | SMALLINT |  | Shaded/direct sunlight flag |  | Solar radiation exposure
SUNINTEN | DOUBLE | W/m² | Solar radiation intensity |  | IEC 60287 solar radiation
SUNABSO | DOUBLE |  | Solar absorptivity coefficient |  | Cable surface solar absorptivity
HEORTE | SMALLINT |  | Heat source or temperature boundary |  | Boundary condition type
HEATEMP | DOUBLE | °C | Heat source temperature |  | Fixed temperature boundary
XLHEAT | DOUBLE | m | Heat source X position |  | X coordinate of external heat source
YLHEAT | DOUBLE | m | Heat source Y position |  | Y coordinate of external heat source
TR_HEATSRC | VARCHAR |  | Transient heat source flag |  | Whether heat source varies with time
HEATSRC_ID | VARCHAR |  | Heat source library ID |  | FK to HEATSRCLIB
HEATSRC_SF | DOUBLE |  | Heat source scale factor |  | Multiplier on library heat rate
DIAHEAT | DOUBLE | m | Heat source diameter |  | Physical size of external heat source
AMBAIR | SMALLINT | °C | Ambient air temperature |  | For cable sections in air
CONVCO | SMALLINT | W/(m²·K) | Convection coefficient |  | For cable-in-air heat transfer
DUCT | VARCHAR |  | Duct flag |  | Whether installation uses ducts
MIGFLAG | VARCHAR |  | Moisture migration flag |  | Whether to model dry-out zone
RHDX | DOUBLE | K.m/W | Dry zone thermal resistivity |  | Soil resistivity in dried-out zone
ISOT | VARCHAR |  | Isothermal surface flag |  | Boundary condition setting
RBOX | DOUBLE |  | Result box display flag (GUI) |  | GUI display option
TRANOPT | SMALLINT |  | Transient option |  | Transient calculation sub-option
IOP | SMALLINT |  | Iterative optimisation parameter |  | Solver tuning
STARTVAL | DOUBLE |  | Parameter sweep start value |  | For parametric studies
ENDVAL | DOUBLE |  | Parameter sweep end value |  | For parametric studies
STEP | DOUBLE |  | Parameter sweep step |  | For parametric studies
ENERGRATE | DOUBLE |  | Energy rate (economic analysis) |  | Cost per kWh
DISCRATE | DOUBLE | % | Discount rate (economic analysis) |  | NPV discount rate
ENERCOST | DOUBLE |  | Energy cost (economic analysis) |  | Total energy cost
DEMDCOST | DOUBLE |  | Demand cost (economic analysis) |  | Peak demand charge
LINCOST | DOUBLE |  | Linear cost (economic analysis) |  | Per-metre cable cost
ECONLIFE | DOUBLE | years | Economic life (economic analysis) |  | Design lifetime
INITINVEST | VARCHAR |  | Initial investment (economic analysis) |  | Capital cost
LENGTH | DOUBLE | m | Cable route length |  | Total cable route length
CHARGING | VARCHAR | A | Charging current |  | Capacitive charging current
INITCURNT | DOUBLE | A | Initial current |  | Starting current for time-varying analysis
LOADGROWTH | DOUBLE | %/yr | Load growth rate |  | Annual load growth
ULTIMLF | DOUBLE |  | Ultimate load factor |  | Long-term target load factor
GROWTHYEAR | DOUBLE | years | Growth period |  | Years over which load grows
WIND | DOUBLE | m/s | Wind speed |  | For cable-in-air convection
WLENGTH | DOUBLE | m | Wavelength parameter |  | For electromagnetic calculation
PERMTR | DOUBLE |  | Perimeter parameter |  | For tunnel/trough calculations
INSTTYPE | SMALLINT |  | Installation type code | 1=Underground, 2=Submarine, etc. | Underground, submarine, air, etc.
DUCTBANK | SMALLINT |  | Duct bank flag |  | Whether duct bank is used
DUCTBANKID | VARCHAR |  | Duct bank library ID reference |  | Links to DUCTLIB table
DUCTYPOS | SMALLINT | m | Duct bank Y position (depth) |  | Depth to duct bank reference point
RHD | DOUBLE | K.m/W | Duct material thermal resistivity |  | Study-level duct thermal resistivity
DUCTNAME | VARCHAR |  | Duct bank name |  | Display name
OFFSETX | DOUBLE | m | Duct bank X offset |  | Horizontal offset of duct bank
OFFSETY | DOUBLE | m | Duct bank Y offset |  | Vertical offset of duct bank
OFFSETX2 | DOUBLE | m | Duct bank X offset (secondary) |  | For two-bank configurations
OFFSETY2 | DOUBLE | m | Duct bank Y offset (secondary) |  | For two-bank configurations
DISTX | DOUBLE | m | Duct X spacing |  | Horizontal distance between ducts
DISTY | DOUBLE | m | Duct Y spacing |  | Vertical distance between ducts
TOTROW | SMALLINT |  | Total duct rows |  | Duct bank row count
TOTCOL | SMALLINT |  | Total duct columns |  | Duct bank column count
DUPIINDI | DOUBLE | m | Duct inside diameter (study-level) |  | Study override for duct ID
DUPIOTDI | DOUBLE | m | Duct outside diameter (study-level) |  | Study override for duct OD
MOISTURE | DOUBLE | % | Critical moisture content |  | Threshold for moisture migration
TRANSIENT | VARCHAR |  | Transient analysis flag |  | Whether transient is enabled
OPTICALC | SMALLINT |  | Optimisation calculation flag |  | Whether to optimise
OPTICIRCNO | SMALLINT |  | Optimisation circuit number |  | Which circuit to optimise
CHOTE_COMPATIBLE | VARCHAR |  | CHOTE compatibility flag |  | Compatibility with CHOTE format
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp
AutoRefCircuitFlag | SMALLINT |  | Auto-reference circuit flag |  | Automatic reference circuit selection
CHOTE_TIMELINE_DATE | VARCHAR |  | CHOTE timeline date |  | Timeline reference date
HEATSOURCE_INSULATION_FLAG | INTEGER |  | Heat source insulation flag |  | Whether heat source has insulation
INSUDIAM_HEATSOURCE | DOUBLE | m | Heat source insulation diameter |  | Insulation OD of heat source
THRESIS_HEATSOURCE | DOUBLE | K.m/W | Heat source insulation thermal resistivity |  | Insulation of heat source
POWERFACTOR | DOUBLE |  | Power factor |  | For AC power calculation
LAGGING_LEADING_FLAG | INTEGER |  | Lagging/leading power factor flag |  | 0=Lagging, 1=Leading
TUNNEL_IMAGE_CHOSEN | INTEGER |  | Tunnel image selection (GUI) |  | GUI display
TUNNEL_CABLETYPE_CHOSEN | INTEGER |  | Tunnel cable type selection |  | Cable arrangement in tunnel
TUNNEL_DIAM | DOUBLE | m | Tunnel diameter |  | For tunnel installation
TUNNEL_ESTHECTIC_PARAM | INTEGER |  | Tunnel aesthetic parameter (GUI) |  | GUI display
CYCLIC_LOADING | INTEGER |  | Cyclic loading flag |  | Whether cyclic loading is applied
EMF_XMIN | DOUBLE | m | EMF calculation X minimum |  | EMF field calculation range
EMF_XMAX | DOUBLE | m | EMF calculation X maximum |  | EMF field calculation range
EMF_XSTEP | DOUBLE | m | EMF calculation X step |  | EMF field calculation resolution
EMF_YVALUES | VARCHAR |  | EMF Y values (serialized) |  | EMF field Y coordinates
TF_LEVEL_VALUES | VARCHAR |  | Temperature field contour levels |  | Thermal field visualisation
TF_LEVEL_COLORS | VARCHAR |  | Temperature field contour colours |  | Thermal field visualisation
TF_LABEL_SPACING | INTEGER |  | Temperature field label spacing |  | Thermal field visualisation
TF_RESOLUTION | DOUBLE |  | Temperature field resolution |  | Thermal field grid resolution
TF_ZOOMOUT_POSITION | INTEGER |  | Temperature field zoom position (GUI) |  | GUI display
TG_FRAME_LEFTPOS | DOUBLE | m | Trough/gutter frame left position |  | Trough geometry
TG_FRAME_TOPPOS | DOUBLE | m | Trough/gutter frame top position |  | Trough geometry
TG_FRAME_WIDTH | DOUBLE | m | Trough/gutter frame width |  | Trough geometry
TG_FRAME_HEIGHT | DOUBLE | m | Trough/gutter frame height |  | Trough geometry
TG_FRAME_THRESIS | DOUBLE | K.m/W | Trough/gutter frame thermal resistivity |  | Trough material
TG_INSIDE_TEXTURE | INTEGER |  | Trough inside texture (GUI) |  | GUI display
TG_FRAME_TEXTURE | INTEGER |  | Trough frame texture (GUI) |  | GUI display
CROSSINGS_FLAG | VARCHAR |  | Cable crossings flag |  | Whether cable crossings are modelled
HEATSOURCE_COLD_OR_HOT | INTEGER |  | Heat source hot/cold flag |  | Whether source heats or cools
CASINGID | VARCHAR |  | Casing library ID |  | FK to CASINGLIB
MULTCASING_INSTALLATION_TYPE | INTEGER |  | Multiple casing installation type |  | Configuration
DEPTH_OF_SEABED | DOUBLE | m | Depth of seabed |  | For submarine cable installation
EARTH_RESISTIVITY | DOUBLE | ohm.m | Earth electrical resistivity |  | For grounding calculations
COMMON_FREQUENCY_FLAG | INTEGER |  | Common frequency flag |  | Whether all cables share same frequency
CABLE_RESISTANCE_FLAG | INTEGER |  | Cable resistance calculation flag |  | How AC resistance is computed
USE_ENLARGE_BOUNDARIES | VARCHAR |  | Enlarged boundaries flag |  | FEM boundary extension
ENLARGE_BOUNDARIES_VALUE | DOUBLE |  | Enlarged boundaries value |  | FEM boundary multiplier
ELECTRICAL_INTERATIVE_BETWEEN_CCTS | VARCHAR |  | Electrical interaction between circuits flag |  | Inter-circuit coupling
TG_SHALLOW_TROUGHS_METHOD | INTEGER |  | Shallow troughs calculation method |  | IEC method selection
CUSTOM_GENERAL_RATINGS_FLAG | INTEGER |  | Custom general ratings flag |  | Override standard ratings
CABLEPARTS_TO_ITERATE_FLAG | INTEGER |  | Cable parts iteration flag |  | Which parts to iterate on
DUCTBANK_CUSTOM_U | DOUBLE |  | Custom duct bank parameter U |  | Custom thermal coefficient
DUCTBANK_CUSTOM_V | DOUBLE |  | Custom duct bank parameter V |  | Custom thermal coefficient
DUCTBANK_CUSTOM_Y | DOUBLE |  | Custom duct bank parameter Y |  | Custom thermal coefficient
STD_NOMINAL_DUCT | INTEGER |  | Standard nominal duct size |  | Nominal duct designation
CLEARANCES_MODE | INTEGER |  | Clearances calculation mode |  | How clearances are computed
TF_STEP_RESOLUTION | DOUBLE |  | Temperature field step resolution |  | FEM mesh refinement
MEDIUM_DUCT_FLAG | INTEGER |  | Medium duct flag |  | Duct fill medium type
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property calculation flag |  | Include magnetic effects
COND_TEMP_OVERLIMIT_FLAG | INTEGER |  | Conductor temperature over-limit flag |  | Warning/constraint
TUNNEL_VENTILATED_FLAG | INTEGER |  | Tunnel ventilation flag |  | Whether tunnel has forced air
AIR_VELOCITY_IN_TUNNEL | DOUBLE | m/s | Air velocity in tunnel |  | Forced ventilation speed
TEMP_OF_AIR_IN_TUNNEL | DOUBLE | °C | Air temperature in tunnel |  | Inlet air temperature
LENGTH_OF_TUNNEL | DOUBLE | m | Tunnel length |  | Total tunnel length
SHAPE_OF_TUNNEL | INTEGER |  | Tunnel cross-section shape |  | Circular, rectangular, etc.
INNER_DIAM_OF_TUNNEL | DOUBLE | m | Inner diameter of tunnel |  | For circular tunnels
IEC_SCOPE_EXTENDED_FLAG | INTEGER |  | IEC extended scope flag |  | Whether extended IEC methods are used
RAC_FACTOR_MAGNETIC_DUCT | DOUBLE |  | AC resistance factor for magnetic duct |  | Correction factor
DUCT_FILLING_TH_RESIS | DOUBLE | K.m/W | Duct filling thermal resistivity |  | Thermal resistivity of duct fill
MDB_DUCTS_TREFOIL_RECALC_FLAG | INTEGER |  | Duct trefoil recalculation flag |  | Force recalculation
COMPUTE_SOLAR_RADIATION_FLAG | INTEGER |  | Compute solar radiation flag |  | Whether to include solar heating
SUNINTEN_PERPENDICULAR | DOUBLE | W/m² | Perpendicular solar radiation intensity |  | Solar flux normal to cable
ANGLE_INCIDENCE | INTEGER | ° | Angle of solar incidence |  | Sun angle to cable surface
FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR_FLAG | INTEGER |  | RAC magnetic armour factor flag |  | IEC correction flag
FACTOR_RAC_DUE_TO_MAGNETIC_DUCT_FLAG | INTEGER |  | RAC magnetic duct factor flag |  | IEC correction flag
FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR_FLAG | INTEGER |  | Lambda1 magnetic armour factor flag |  | IEC correction flag
FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT_FLAG | INTEGER |  | Lambda1 magnetic duct factor flag |  | IEC correction flag
FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING_FLAG | INTEGER |  | Lambda2-to-lambda1 circulating factor flag |  | IEC correction flag
LAMBDA1_EDDY_COMPUTATION_FLAG | INTEGER |  | Lambda1 eddy current computation flag |  | IEC loss calculation method
LAMBDA2_PIPE_COMPUTATION_FLAG | INTEGER |  | Lambda2 pipe computation flag |  | IEC loss calculation method
WD_COMPUTATION_FLAG | INTEGER |  | Wd (dielectric loss) computation flag |  | IEC loss calculation method
T4_COMPUTATION_FLAG | INTEGER |  | T4 (external thermal resistance) computation flag |  | IEC method
CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR | DOUBLE |  | Custom RAC factor for magnetic armour |  | User override value
CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_DUCT | DOUBLE |  | Custom RAC factor for magnetic duct |  | User override value
CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR | DOUBLE |  | Custom lambda1 factor for magnetic armour |  | User override value
CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT | DOUBLE |  | Custom lambda1 factor for magnetic duct |  | User override value
CUSTOM_FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING | DOUBLE |  | Custom lambda2-to-lambda1 circulating factor |  | User override value
GENERAL_GUIDANCE_FLAG | INTEGER |  | General guidance/notes flag |  | Whether guidance notes are shown
T2_COMPUTATION_FLAG | INTEGER |  | T2 (between sheath and armour) computation flag |  | IEC method
ENVIRONMENT_CONFIG_ID | VARCHAR |  | Environment configuration ID |  | FK to GLOBAL_ENVIRONMENT_PARAMETERS
ENVIRONMENT_OFFSET_AMBIENT | DOUBLE | °C | Ambient temperature offset |  | Adjustment to environment config ambient
CABIN_JTUBE_FLAG | VARCHAR |  | Cable in J-tube flag |  | For J-tube installations
JTUBE_LENGTH_ABOVE_WATER | DOUBLE | m | J-tube length above water |  | Exposed J-tube section
CAB_IMMERSED_IN_WATER_FLAG | VARCHAR |  | Cable immersed in water flag |  | Submarine section flag
HIGH_VOLTAGE_DC_CABLE_FLAG | VARCHAR |  | HVDC cable flag |  | For DC-specific calculations
TUNNELWALL_ADVANCED_FLAG | INTEGER |  | Advanced tunnel wall modelling flag |  | Detailed wall thermal model
TUNNELWALL_THICKNESS | DOUBLE | m | Tunnel wall thickness |  | For wall thermal resistance
TUNNELWALL_THERMALRESIS | DOUBLE | K.m/W | Tunnel wall thermal resistivity |  | Wall material property

## SHAPEWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYSHAPE | VARCHAR |  | Shape ID — unique identifier |  | Primary key, VARCHAR
TITLE | VARCHAR |  | Shape title |  | User-entered label
T0 | DOUBLE | h | Time point 0 (hour offset from midnight) |  | 24-hour load shape time coordinate
I0 | DOUBLE | p.u. | Load at time point 0 (per unit of base amps) |  | 24-hour load shape current value
T1 | DOUBLE | h | Time point 1 (hour offset from midnight) |  | 24-hour load shape time coordinate
I1 | DOUBLE | p.u. | Load at time point 1 (per unit of base amps) |  | 24-hour load shape current value
T2 | DOUBLE | h | Time point 2 (hour offset from midnight) |  | 24-hour load shape time coordinate
I2 | DOUBLE | p.u. | Load at time point 2 (per unit of base amps) |  | 24-hour load shape current value
T3 | DOUBLE | h | Time point 3 (hour offset from midnight) |  | 24-hour load shape time coordinate
I3 | DOUBLE | p.u. | Load at time point 3 (per unit of base amps) |  | 24-hour load shape current value
T4 | DOUBLE | h | Time point 4 (hour offset from midnight) |  | 24-hour load shape time coordinate
I4 | DOUBLE | p.u. | Load at time point 4 (per unit of base amps) |  | 24-hour load shape current value
T5 | DOUBLE | h | Time point 5 (hour offset from midnight) |  | 24-hour load shape time coordinate
I5 | DOUBLE | p.u. | Load at time point 5 (per unit of base amps) |  | 24-hour load shape current value
T6 | DOUBLE | h | Time point 6 (hour offset from midnight) |  | 24-hour load shape time coordinate
I6 | DOUBLE | p.u. | Load at time point 6 (per unit of base amps) |  | 24-hour load shape current value
T7 | DOUBLE | h | Time point 7 (hour offset from midnight) |  | 24-hour load shape time coordinate
I7 | DOUBLE | p.u. | Load at time point 7 (per unit of base amps) |  | 24-hour load shape current value
T8 | DOUBLE | h | Time point 8 (hour offset from midnight) |  | 24-hour load shape time coordinate
I8 | DOUBLE | p.u. | Load at time point 8 (per unit of base amps) |  | 24-hour load shape current value
T9 | DOUBLE | h | Time point 9 (hour offset from midnight) |  | 24-hour load shape time coordinate
I9 | DOUBLE | p.u. | Load at time point 9 (per unit of base amps) |  | 24-hour load shape current value
T10 | DOUBLE | h | Time point 10 (hour offset from midnight) |  | 24-hour load shape time coordinate
I10 | DOUBLE | p.u. | Load at time point 10 (per unit of base amps) |  | 24-hour load shape current value
T11 | DOUBLE | h | Time point 11 (hour offset from midnight) |  | 24-hour load shape time coordinate
I11 | DOUBLE | p.u. | Load at time point 11 (per unit of base amps) |  | 24-hour load shape current value
T12 | DOUBLE | h | Time point 12 (hour offset from midnight) |  | 24-hour load shape time coordinate
I12 | DOUBLE | p.u. | Load at time point 12 (per unit of base amps) |  | 24-hour load shape current value
T13 | DOUBLE | h | Time point 13 (hour offset from midnight) |  | 24-hour load shape time coordinate
I13 | DOUBLE | p.u. | Load at time point 13 (per unit of base amps) |  | 24-hour load shape current value
T14 | DOUBLE | h | Time point 14 (hour offset from midnight) |  | 24-hour load shape time coordinate
I14 | DOUBLE | p.u. | Load at time point 14 (per unit of base amps) |  | 24-hour load shape current value
T15 | DOUBLE | h | Time point 15 (hour offset from midnight) |  | 24-hour load shape time coordinate
I15 | DOUBLE | p.u. | Load at time point 15 (per unit of base amps) |  | 24-hour load shape current value
T16 | DOUBLE | h | Time point 16 (hour offset from midnight) |  | 24-hour load shape time coordinate
I16 | DOUBLE | p.u. | Load at time point 16 (per unit of base amps) |  | 24-hour load shape current value
T17 | DOUBLE | h | Time point 17 (hour offset from midnight) |  | 24-hour load shape time coordinate
I17 | DOUBLE | p.u. | Load at time point 17 (per unit of base amps) |  | 24-hour load shape current value
T18 | DOUBLE | h | Time point 18 (hour offset from midnight) |  | 24-hour load shape time coordinate
I18 | DOUBLE | p.u. | Load at time point 18 (per unit of base amps) |  | 24-hour load shape current value
T19 | DOUBLE | h | Time point 19 (hour offset from midnight) |  | 24-hour load shape time coordinate
I19 | DOUBLE | p.u. | Load at time point 19 (per unit of base amps) |  | 24-hour load shape current value
T20 | DOUBLE | h | Time point 20 (hour offset from midnight) |  | 24-hour load shape time coordinate
I20 | DOUBLE | p.u. | Load at time point 20 (per unit of base amps) |  | 24-hour load shape current value
T21 | DOUBLE | h | Time point 21 (hour offset from midnight) |  | 24-hour load shape time coordinate
I21 | DOUBLE | p.u. | Load at time point 21 (per unit of base amps) |  | 24-hour load shape current value
T22 | DOUBLE | h | Time point 22 (hour offset from midnight) |  | 24-hour load shape time coordinate
I22 | DOUBLE | p.u. | Load at time point 22 (per unit of base amps) |  | 24-hour load shape current value
T23 | DOUBLE | h | Time point 23 (hour offset from midnight) |  | 24-hour load shape time coordinate
I23 | DOUBLE | p.u. | Load at time point 23 (per unit of base amps) |  | 24-hour load shape current value
SHAPETYPE | SMALLINT |  | Shape type code |  | Type of daily load shape
LOADFACT | DOUBLE |  | Load factor for this shape |  | Average/peak ratio
TAG | VARCHAR |  | Record tag |  | Internal flag
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp
DATA_PAGE | INTEGER |  | Data page reference (GUI) |  | Which GUI tab the data is on

## LOADWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYLOAD | VARCHAR |  | Load window ID — unique identifier |  | Primary key, VARCHAR
TITLE | VARCHAR |  | Load window title |  | User-entered label
OLDKEY | VARCHAR |  | Legacy key (migration reference) |  | For backwards compatibility
FNAME | VARCHAR |  | Source filename |  | Original data file reference
STARTDATE | VARCHAR |  | Load profile start date |  | Date string for load profile start
BASEAMPS | DOUBLE | A | Base ampacity / peak current |  | Reference current for per-unit load shapes
TAG | VARCHAR |  | Record tag |  | Internal flag
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp
AVERAGE_LOADFACTOR | DOUBLE |  | Average load factor (calculated) |  | Mean of daily load factors across profile

## DUCTLIB
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
DUCTBANKID | VARCHAR |  | Duct bank ID — unique identifier |  | Primary key, VARCHAR
DUCTBANK | VARCHAR |  | Duct bank name/title |  | User-entered label
TAG | VARCHAR |  | Record tag |  | Internal flag
HEIGHT | DOUBLE | m | Duct bank overall height |  | Vertical extent of encasement
WIDTH | DOUBLE | m | Duct bank overall width |  | Horizontal extent of encasement
AXB | DOUBLE |  | Duct bank drawing axis parameter (GUI) |  | Cross-section display
ALB | DOUBLE |  | Duct bank drawing scale parameter (GUI) |  | Cross-section display
OFFSETX | DOUBLE | m | X offset of duct array from bank centre |  | Duct positioning
OFFSETY | DOUBLE | m | Y offset of duct array from bank centre |  | Duct positioning
OFFSETX2 | DOUBLE | m | X offset (secondary array) |  | For multi-array banks
OFFSETY2 | DOUBLE | m | Y offset (secondary array) |  | For multi-array banks
DISTX | DOUBLE | m | Horizontal spacing between duct centres |  | Duct pitch X
DISTY | DOUBLE | m | Vertical spacing between duct centres |  | Duct pitch Y
TOTROW | SMALLINT |  | Total number of duct rows |  | Bank layout
TOTCOL | SMALLINT |  | Total number of duct columns |  | Bank layout
DUPIOTDI | DOUBLE | m | Duct outside diameter |  | External diameter of duct conduit
DUPIINDI | DOUBLE | m | Duct inside diameter |  | Internal diameter of duct conduit
XAXISORGM | DOUBLE | m | X axis origin (metric, GUI) |  | Drawing coordinate
XAXISLENM | DOUBLE | m | X axis length (metric, GUI) |  | Drawing coordinate
XAXISSTEPM | DOUBLE | m | X axis step (metric, GUI) |  | Drawing coordinate
YAXISORGM | DOUBLE | m | Y axis origin (metric, GUI) |  | Drawing coordinate
YAXISLENM | DOUBLE | m | Y axis length (metric, GUI) |  | Drawing coordinate
YAXISSTEPM | DOUBLE | m | Y axis step (metric, GUI) |  | Drawing coordinate
XAXISORGI | DOUBLE | in | X axis origin (imperial, GUI) |  | Drawing coordinate
XAXISLENI | DOUBLE | in | X axis length (imperial, GUI) |  | Drawing coordinate
XAXISSTEPI | DOUBLE | in | X axis step (imperial, GUI) |  | Drawing coordinate
YAXISORGI | DOUBLE | in | Y axis origin (imperial, GUI) |  | Drawing coordinate
YAXISLENI | DOUBLE | in | Y axis length (imperial, GUI) |  | Drawing coordinate
YAXISSTEPI | DOUBLE | in | Y axis step (imperial, GUI) |  | Drawing coordinate
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp
STD_NOMINAL_DUCT | INTEGER |  | Standard nominal duct size designation |  | Duct product standard
CLEARANCES_MODE | INTEGER |  | Clearances calculation mode |  | How clearances are computed

## TRANSIEN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | SMALLINT |  | Execution number |  | Sub-case identifier
TAG | VARCHAR |  | Record tag |  | Internal flag
TRANSELCT | SMALLINT |  | Transient selection type |  | Which transient analysis to run
TEMP | SMALLINT | °C | Target/initial temperature |  | Starting or target conductor temperature
TIMEREQ | DOUBLE | h | Time required |  | Duration of transient event
LCURV | DOUBLE |  | Load curve type |  | Shape of transient load profile
SRCH1 | DOUBLE |  | Search parameter 1 |  | Solver search control
SRCH2 | DOUBLE |  | Search parameter 2 |  | Solver search control
RANGT1 | DOUBLE |  | Range parameter T1 |  | Temperature/time range bound
RANGT2 | DOUBLE |  | Range parameter T2 |  | Temperature/time range bound
SCALE1 | DOUBLE |  | Scale parameter 1 |  | Solver scaling
SCALE2 | DOUBLE |  | Scale parameter 2 |  | Solver scaling
RESSC1 | DOUBLE |  | Result scaling parameter |  | Output scaling
REST1 | DOUBLE |  | Result time parameter |  | Output time range
SOLVTYPOP1 | SMALLINT |  | Solver type option |  | Solver algorithm selection
PARTICDATA | VARCHAR |  | Particular data (serialized) |  | Additional transient parameters
SCFACTDATA | VARCHAR |  | Scale factor data (serialized) |  | Time-dependent scale factors
DESTEMDATA | VARCHAR |  | Design temperature data (serialized) |  | Temperature constraints
COMTYP | SMALLINT |  | Computation type |  | Detailed calculation method
IDLOAD1 | VARCHAR |  | Load window ID for cable 1 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD2 | VARCHAR |  | Load window ID for cable 2 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD3 | VARCHAR |  | Load window ID for cable 3 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD4 | VARCHAR |  | Load window ID for cable 4 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD5 | VARCHAR |  | Load window ID for cable 5 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD6 | VARCHAR |  | Load window ID for cable 6 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD7 | VARCHAR |  | Load window ID for cable 7 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD8 | VARCHAR |  | Load window ID for cable 8 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD9 | VARCHAR |  | Load window ID for cable 9 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD10 | VARCHAR |  | Load window ID for cable 10 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD11 | VARCHAR |  | Load window ID for cable 11 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD12 | VARCHAR |  | Load window ID for cable 12 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD13 | VARCHAR |  | Load window ID for cable 13 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD14 | VARCHAR |  | Load window ID for cable 14 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD15 | VARCHAR |  | Load window ID for cable 15 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD16 | VARCHAR |  | Load window ID for cable 16 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD17 | VARCHAR |  | Load window ID for cable 17 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD18 | VARCHAR |  | Load window ID for cable 18 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD19 | VARCHAR |  | Load window ID for cable 19 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD20 | VARCHAR |  | Load window ID for cable 20 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD21 | VARCHAR |  | Load window ID for cable 21 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD22 | VARCHAR |  | Load window ID for cable 22 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD23 | VARCHAR |  | Load window ID for cable 23 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD24 | VARCHAR |  | Load window ID for cable 24 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD25 | VARCHAR |  | Load window ID for cable 25 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD26 | VARCHAR |  | Load window ID for cable 26 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD27 | VARCHAR |  | Load window ID for cable 27 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD28 | VARCHAR |  | Load window ID for cable 28 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD29 | VARCHAR |  | Load window ID for cable 29 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD30 | VARCHAR |  | Load window ID for cable 30 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD31 | VARCHAR |  | Load window ID for cable 31 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD32 | VARCHAR |  | Load window ID for cable 32 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD33 | VARCHAR |  | Load window ID for cable 33 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD34 | VARCHAR |  | Load window ID for cable 34 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD35 | VARCHAR |  | Load window ID for cable 35 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD36 | VARCHAR |  | Load window ID for cable 36 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD37 | VARCHAR |  | Load window ID for cable 37 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD38 | VARCHAR |  | Load window ID for cable 38 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD39 | VARCHAR |  | Load window ID for cable 39 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD40 | VARCHAR |  | Load window ID for cable 40 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD41 | VARCHAR |  | Load window ID for cable 41 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD42 | VARCHAR |  | Load window ID for cable 42 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD43 | VARCHAR |  | Load window ID for cable 43 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD44 | VARCHAR |  | Load window ID for cable 44 |  | FK to LOADWIN — assigns load profile to cable position
IDLOAD45 | VARCHAR |  | Load window ID for cable 45 |  | FK to LOADWIN — assigns load profile to cable position
FACT1 | DOUBLE |  | Load scale factor for cable 1 |  | Multiplier on load profile for this cable
FACT2 | DOUBLE |  | Load scale factor for cable 2 |  | Multiplier on load profile for this cable
FACT3 | DOUBLE |  | Load scale factor for cable 3 |  | Multiplier on load profile for this cable
FACT4 | DOUBLE |  | Load scale factor for cable 4 |  | Multiplier on load profile for this cable
FACT5 | DOUBLE |  | Load scale factor for cable 5 |  | Multiplier on load profile for this cable
FACT6 | DOUBLE |  | Load scale factor for cable 6 |  | Multiplier on load profile for this cable
FACT7 | DOUBLE |  | Load scale factor for cable 7 |  | Multiplier on load profile for this cable
FACT8 | DOUBLE |  | Load scale factor for cable 8 |  | Multiplier on load profile for this cable
FACT9 | DOUBLE |  | Load scale factor for cable 9 |  | Multiplier on load profile for this cable
FACT10 | DOUBLE |  | Load scale factor for cable 10 |  | Multiplier on load profile for this cable
FACT11 | DOUBLE |  | Load scale factor for cable 11 |  | Multiplier on load profile for this cable
FACT12 | DOUBLE |  | Load scale factor for cable 12 |  | Multiplier on load profile for this cable
FACT13 | DOUBLE |  | Load scale factor for cable 13 |  | Multiplier on load profile for this cable
FACT14 | DOUBLE |  | Load scale factor for cable 14 |  | Multiplier on load profile for this cable
FACT15 | DOUBLE |  | Load scale factor for cable 15 |  | Multiplier on load profile for this cable
FACT16 | DOUBLE |  | Load scale factor for cable 16 |  | Multiplier on load profile for this cable
FACT17 | DOUBLE |  | Load scale factor for cable 17 |  | Multiplier on load profile for this cable
FACT18 | DOUBLE |  | Load scale factor for cable 18 |  | Multiplier on load profile for this cable
FACT19 | DOUBLE |  | Load scale factor for cable 19 |  | Multiplier on load profile for this cable
FACT20 | DOUBLE |  | Load scale factor for cable 20 |  | Multiplier on load profile for this cable
FACT21 | DOUBLE |  | Load scale factor for cable 21 |  | Multiplier on load profile for this cable
FACT22 | DOUBLE |  | Load scale factor for cable 22 |  | Multiplier on load profile for this cable
FACT23 | DOUBLE |  | Load scale factor for cable 23 |  | Multiplier on load profile for this cable
FACT24 | DOUBLE |  | Load scale factor for cable 24 |  | Multiplier on load profile for this cable
FACT25 | DOUBLE |  | Load scale factor for cable 25 |  | Multiplier on load profile for this cable
FACT26 | DOUBLE |  | Load scale factor for cable 26 |  | Multiplier on load profile for this cable
FACT27 | DOUBLE |  | Load scale factor for cable 27 |  | Multiplier on load profile for this cable
FACT28 | DOUBLE |  | Load scale factor for cable 28 |  | Multiplier on load profile for this cable
FACT29 | DOUBLE |  | Load scale factor for cable 29 |  | Multiplier on load profile for this cable
FACT30 | DOUBLE |  | Load scale factor for cable 30 |  | Multiplier on load profile for this cable
FACT31 | DOUBLE |  | Load scale factor for cable 31 |  | Multiplier on load profile for this cable
FACT32 | DOUBLE |  | Load scale factor for cable 32 |  | Multiplier on load profile for this cable
FACT33 | DOUBLE |  | Load scale factor for cable 33 |  | Multiplier on load profile for this cable
FACT34 | DOUBLE |  | Load scale factor for cable 34 |  | Multiplier on load profile for this cable
FACT35 | DOUBLE |  | Load scale factor for cable 35 |  | Multiplier on load profile for this cable
FACT36 | DOUBLE |  | Load scale factor for cable 36 |  | Multiplier on load profile for this cable
FACT37 | DOUBLE |  | Load scale factor for cable 37 |  | Multiplier on load profile for this cable
FACT38 | DOUBLE |  | Load scale factor for cable 38 |  | Multiplier on load profile for this cable
FACT39 | DOUBLE |  | Load scale factor for cable 39 |  | Multiplier on load profile for this cable
FACT40 | DOUBLE |  | Load scale factor for cable 40 |  | Multiplier on load profile for this cable
FACT41 | DOUBLE |  | Load scale factor for cable 41 |  | Multiplier on load profile for this cable
FACT42 | DOUBLE |  | Load scale factor for cable 42 |  | Multiplier on load profile for this cable
FACT43 | DOUBLE |  | Load scale factor for cable 43 |  | Multiplier on load profile for this cable
FACT44 | DOUBLE |  | Load scale factor for cable 44 |  | Multiplier on load profile for this cable
FACT45 | DOUBLE |  | Load scale factor for cable 45 |  | Multiplier on load profile for this cable
TOG1 | SMALLINT |  | Toggle flag for cable 1 |  | Enable/disable this cable in transient calc
TOG2 | SMALLINT |  | Toggle flag for cable 2 |  | Enable/disable this cable in transient calc
TOG3 | SMALLINT |  | Toggle flag for cable 3 |  | Enable/disable this cable in transient calc
TOG4 | SMALLINT |  | Toggle flag for cable 4 |  | Enable/disable this cable in transient calc
TOG5 | SMALLINT |  | Toggle flag for cable 5 |  | Enable/disable this cable in transient calc
TOG6 | SMALLINT |  | Toggle flag for cable 6 |  | Enable/disable this cable in transient calc
TOG7 | SMALLINT |  | Toggle flag for cable 7 |  | Enable/disable this cable in transient calc
TOG8 | SMALLINT |  | Toggle flag for cable 8 |  | Enable/disable this cable in transient calc
TOG9 | SMALLINT |  | Toggle flag for cable 9 |  | Enable/disable this cable in transient calc
TOG10 | SMALLINT |  | Toggle flag for cable 10 |  | Enable/disable this cable in transient calc
TOG11 | SMALLINT |  | Toggle flag for cable 11 |  | Enable/disable this cable in transient calc
TOG12 | SMALLINT |  | Toggle flag for cable 12 |  | Enable/disable this cable in transient calc
TOG13 | SMALLINT |  | Toggle flag for cable 13 |  | Enable/disable this cable in transient calc
TOG14 | SMALLINT |  | Toggle flag for cable 14 |  | Enable/disable this cable in transient calc
TOG15 | SMALLINT |  | Toggle flag for cable 15 |  | Enable/disable this cable in transient calc
TOG16 | SMALLINT |  | Toggle flag for cable 16 |  | Enable/disable this cable in transient calc
TOG17 | SMALLINT |  | Toggle flag for cable 17 |  | Enable/disable this cable in transient calc
TOG18 | SMALLINT |  | Toggle flag for cable 18 |  | Enable/disable this cable in transient calc
TOG19 | SMALLINT |  | Toggle flag for cable 19 |  | Enable/disable this cable in transient calc
TOG20 | SMALLINT |  | Toggle flag for cable 20 |  | Enable/disable this cable in transient calc
TOG21 | SMALLINT |  | Toggle flag for cable 21 |  | Enable/disable this cable in transient calc
TOG22 | SMALLINT |  | Toggle flag for cable 22 |  | Enable/disable this cable in transient calc
TOG23 | SMALLINT |  | Toggle flag for cable 23 |  | Enable/disable this cable in transient calc
TOG24 | SMALLINT |  | Toggle flag for cable 24 |  | Enable/disable this cable in transient calc
TOG25 | SMALLINT |  | Toggle flag for cable 25 |  | Enable/disable this cable in transient calc
TOG26 | SMALLINT |  | Toggle flag for cable 26 |  | Enable/disable this cable in transient calc
TOG27 | SMALLINT |  | Toggle flag for cable 27 |  | Enable/disable this cable in transient calc
TOG28 | SMALLINT |  | Toggle flag for cable 28 |  | Enable/disable this cable in transient calc
TOG29 | SMALLINT |  | Toggle flag for cable 29 |  | Enable/disable this cable in transient calc
TOG30 | SMALLINT |  | Toggle flag for cable 30 |  | Enable/disable this cable in transient calc
TOG31 | SMALLINT |  | Toggle flag for cable 31 |  | Enable/disable this cable in transient calc
TOG32 | SMALLINT |  | Toggle flag for cable 32 |  | Enable/disable this cable in transient calc
TOG33 | SMALLINT |  | Toggle flag for cable 33 |  | Enable/disable this cable in transient calc
TOG34 | SMALLINT |  | Toggle flag for cable 34 |  | Enable/disable this cable in transient calc
TOG35 | SMALLINT |  | Toggle flag for cable 35 |  | Enable/disable this cable in transient calc
TOG36 | SMALLINT |  | Toggle flag for cable 36 |  | Enable/disable this cable in transient calc
TOG37 | SMALLINT |  | Toggle flag for cable 37 |  | Enable/disable this cable in transient calc
TOG38 | SMALLINT |  | Toggle flag for cable 38 |  | Enable/disable this cable in transient calc
TOG39 | SMALLINT |  | Toggle flag for cable 39 |  | Enable/disable this cable in transient calc
TOG40 | SMALLINT |  | Toggle flag for cable 40 |  | Enable/disable this cable in transient calc
TOG41 | SMALLINT |  | Toggle flag for cable 41 |  | Enable/disable this cable in transient calc
TOG42 | SMALLINT |  | Toggle flag for cable 42 |  | Enable/disable this cable in transient calc
TOG43 | SMALLINT |  | Toggle flag for cable 43 |  | Enable/disable this cable in transient calc
TOG44 | SMALLINT |  | Toggle flag for cable 44 |  | Enable/disable this cable in transient calc
TOG45 | SMALLINT |  | Toggle flag for cable 45 |  | Enable/disable this cable in transient calc
EMERCURDATA | VARCHAR |  | Emergency current data (serialized) |  | Emergency overload current profile
DES_SHEATHTEMDATA | CHAR |  | Design sheath temperature data (serialized) |  | Sheath temperature constraints
DES_ARMOURTEMDATA | CHAR |  | Design armour temperature data (serialized) |  | Armour temperature constraints
DES_EXTERIORTEMDATA | CHAR |  | Design exterior temperature data (serialized) |  | External surface temperature constraints
DATAPAGE | INTEGER |  | Data page reference (GUI) |  | Which GUI tab the data is on

## GLOBAL_ENV_PARAM_AMBIENT_VS_DEP
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
ENVIRONMENT_CONFIG_ID | CHAR |  | Config ID — FK to GLOBAL_ENVIRONMENT_PARAMETERS |  | Parent config
ENVIRONMENT_CONFIG_NAME | CHAR |  | Configuration name |  | Denormalized from parent config
DEPTH_RANGE | DOUBLE |  | Depth range category |  | Classification of depth band
AMBIENT_TEMP | DOUBLE | °C | Ambient temperature at this depth |  | Temperature vs depth profile
TAG | CHAR |  | Record tag |  | Internal flag

## HEATSRCLIB
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
HEATSRC_ID | VARCHAR |  | Heat source library ID (alternative key) |  | Alternative identifier
TITLE | VARCHAR |  | Heat source title |  | User-entered label
TAG | VARCHAR |  | Record tag |  | Internal flag
HEORTE | SMALLINT |  | Heat or temperature boundary type |  | Whether source is heat rate or fixed temperature
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp

## GLOBAL_ENVIRONMENT_PARAMETERS
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
ENVIRONMENT_CONFIG_ID | CHAR |  | Configuration ID — unique identifier |  | Primary key, VARCHAR
ENVIRONMENT_CONFIG_NAME | CHAR |  | Configuration name |  | User-entered label
AMBIENT | DOUBLE | °C | Ambient soil temperature |  | Default ambient for studies using this config
RHOS | DOUBLE | K.m/W | Native soil thermal resistivity |  | Default soil thermal resistivity
DEPTH_FLAG | CHAR |  | Depth calculation flag |  | How burial depth is handled
ISOT | CHAR |  | Isothermal surface flag |  | Boundary condition setting
AMBAIR | INTEGER | °C | Ambient air temperature |  | For cable sections in air
MIGFLAG | CHAR |  | Moisture migration flag |  | Whether to model dry-out zone
RHDX | DOUBLE | K.m/W | Dry zone thermal resistivity |  | Soil resistivity in dried-out zone
MOISTURE | DOUBLE | % | Critical moisture content |  | Threshold for moisture migration
TAG | CHAR |  | Record tag |  | Internal flag

## VERSION
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
VERSION | CHAR |  | CYMCAP database schema version string |  | Tracks DB format version

## ALSSS
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Links to parent study
EXECUNO | SMALLINT |  | Execution number |  | Sub-case identifier
IDCAB | VARCHAR |  | Cable ID — foreign key to CABLES |  | Which cable these results are for
TAG | VARCHAR |  | Record tag |  | Internal flag
ALS1 | DOUBLE | A | Ampacity result 1 |  | Rated current for calculation case
SS1 | DOUBLE | °C | Steady-state temperature result 1 |  | Maximum conductor temperature
ALS2 | DOUBLE | A | Ampacity result 2 |  | Rated current for calculation case
SS2 | DOUBLE | °C | Steady-state temperature result 2 |  | Maximum conductor temperature
ALS3 | DOUBLE | A | Ampacity result 3 |  | Rated current for calculation case
SS3 | DOUBLE | °C | Steady-state temperature result 3 |  | Maximum conductor temperature
ALS4 | DOUBLE | A | Ampacity result 4 |  | Rated current for calculation case
SS4 | DOUBLE | °C | Steady-state temperature result 4 |  | Maximum conductor temperature
ALS5 | DOUBLE | A | Ampacity result 5 |  | Rated current for calculation case
SS5 | DOUBLE | °C | Steady-state temperature result 5 |  | Maximum conductor temperature
ALS6 | DOUBLE | A | Ampacity result 6 |  | Rated current for calculation case
SS6 | DOUBLE | °C | Steady-state temperature result 6 |  | Maximum conductor temperature
ALS7 | DOUBLE | A | Ampacity result 7 |  | Rated current for calculation case
SS7 | DOUBLE | °C | Steady-state temperature result 7 |  | Maximum conductor temperature
ALS8 | DOUBLE | A | Ampacity result 8 |  | Rated current for calculation case
SS8 | DOUBLE | °C | Steady-state temperature result 8 |  | Maximum conductor temperature
ALS9 | DOUBLE | A | Ampacity result 9 |  | Rated current for calculation case
SS9 | DOUBLE | °C | Steady-state temperature result 9 |  | Maximum conductor temperature
ALS10 | DOUBLE | A | Ampacity result 10 |  | Rated current for calculation case
SS10 | DOUBLE | °C | Steady-state temperature result 10 |  | Maximum conductor temperature

## CASINGLIB
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
CASINGID | CHAR |  | Casing ID — unique identifier |  | Primary key
CASING_NAME | CHAR |  | Casing name |  | User-entered casing label
TAG | CHAR |  | Record tag |  | Internal flag
XCENTRE | DOUBLE | m | Casing centre X coordinate |  | Horizontal position
YCENTRE | DOUBLE | m | Casing centre Y coordinate (depth) |  | Vertical position
NBDUCTS | INTEGER |  | Number of ducts in casing |  | Duct count within casing
DISTRAD | DOUBLE | m | Radial distance of ducts from casing centre |  | Duct positioning radius
STARTANGLE | DOUBLE | ° | Starting angle for duct arrangement |  | Angular offset for first duct
DUCTS_TOUCHING | CHAR |  | Ducts touching flag |  | Whether ducts are in contact
CENTRE_DUCT | CHAR |  | Centre duct flag |  | Whether there is a centre duct
DUPIOTDI | DOUBLE | m | Duct outside diameter |  | External diameter of duct conduit
DUPIINDI | DOUBLE | m | Duct inside diameter |  | Internal diameter of duct conduit
CASINGINDI | DOUBLE | m | Casing inside diameter (alternative) |  | Casing bore dimension
CASINGOTDI | DOUBLE | m | Casing outside diameter (alternative) |  | Casing OD dimension
STD_NOMINAL_DUCT | INTEGER |  | Standard nominal duct size |  | Duct product standard
LOCKEDBY | CHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | CHAR |  | Lock timestamp |  | Multi-user locking timestamp

## HISTORICAL_DAYWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYLOAD | VARCHAR |  | Load window ID |  | Same as DAYWIN
KEYSHAPE | VARCHAR |  | Shape ID |  | Same as DAYWIN
SF | DOUBLE |  | Scale factor |  | Same as DAYWIN
ORDER_NO | VARCHAR |  | Day order number |  | Same as DAYWIN
HISTORICAL_DATA_FLAG | SMALLINT |  | Historical data flag |  | Whether this is archived historical data
TAG | VARCHAR |  | Record tag |  | Internal flag

## HISTORICAL_LOADWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYLOAD | VARCHAR |  | Load window ID |  | Same as LOADWIN.KEYLOAD
TITLE | VARCHAR |  | Load window title |  | Same as LOADWIN
OLDKEY | VARCHAR |  | Legacy key |  | Same as LOADWIN
FNAME | VARCHAR |  | Source filename |  | Same as LOADWIN
STARTDATE | VARCHAR |  | Start date |  | Same as LOADWIN
BASEAMPS | DOUBLE | A | Base ampacity |  | Same as LOADWIN
HISTORICAL_DATA_FLAG | SMALLINT |  | Historical data flag |  | Whether this is archived historical data
TAG | VARCHAR |  | Record tag |  | Internal flag
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp

## HISTORICAL_SHAPEWIN
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
KEYSHAPE | VARCHAR |  | Shape ID |  | Same as SHAPEWIN.KEYSHAPE
TITLE | VARCHAR |  | Shape title |  | Same as SHAPEWIN
T0 | DOUBLE | h | Time point 0 |  | Same as SHAPEWIN
I0 | DOUBLE | p.u. | Load at time point 0 |  | Same as SHAPEWIN
T1 | DOUBLE | h | Time point 1 |  | Same as SHAPEWIN
I1 | DOUBLE | p.u. | Load at time point 1 |  | Same as SHAPEWIN
T2 | DOUBLE | h | Time point 2 |  | Same as SHAPEWIN
I2 | DOUBLE | p.u. | Load at time point 2 |  | Same as SHAPEWIN
T3 | DOUBLE | h | Time point 3 |  | Same as SHAPEWIN
I3 | DOUBLE | p.u. | Load at time point 3 |  | Same as SHAPEWIN
T4 | DOUBLE | h | Time point 4 |  | Same as SHAPEWIN
I4 | DOUBLE | p.u. | Load at time point 4 |  | Same as SHAPEWIN
T5 | DOUBLE | h | Time point 5 |  | Same as SHAPEWIN
I5 | DOUBLE | p.u. | Load at time point 5 |  | Same as SHAPEWIN
T6 | DOUBLE | h | Time point 6 |  | Same as SHAPEWIN
I6 | DOUBLE | p.u. | Load at time point 6 |  | Same as SHAPEWIN
T7 | DOUBLE | h | Time point 7 |  | Same as SHAPEWIN
I7 | DOUBLE | p.u. | Load at time point 7 |  | Same as SHAPEWIN
T8 | DOUBLE | h | Time point 8 |  | Same as SHAPEWIN
I8 | DOUBLE | p.u. | Load at time point 8 |  | Same as SHAPEWIN
T9 | DOUBLE | h | Time point 9 |  | Same as SHAPEWIN
I9 | DOUBLE | p.u. | Load at time point 9 |  | Same as SHAPEWIN
T10 | DOUBLE | h | Time point 10 |  | Same as SHAPEWIN
I10 | DOUBLE | p.u. | Load at time point 10 |  | Same as SHAPEWIN
T11 | DOUBLE | h | Time point 11 |  | Same as SHAPEWIN
I11 | DOUBLE | p.u. | Load at time point 11 |  | Same as SHAPEWIN
T12 | DOUBLE | h | Time point 12 |  | Same as SHAPEWIN
I12 | DOUBLE | p.u. | Load at time point 12 |  | Same as SHAPEWIN
T13 | DOUBLE | h | Time point 13 |  | Same as SHAPEWIN
I13 | DOUBLE | p.u. | Load at time point 13 |  | Same as SHAPEWIN
T14 | DOUBLE | h | Time point 14 |  | Same as SHAPEWIN
I14 | DOUBLE | p.u. | Load at time point 14 |  | Same as SHAPEWIN
T15 | DOUBLE | h | Time point 15 |  | Same as SHAPEWIN
I15 | DOUBLE | p.u. | Load at time point 15 |  | Same as SHAPEWIN
T16 | DOUBLE | h | Time point 16 |  | Same as SHAPEWIN
I16 | DOUBLE | p.u. | Load at time point 16 |  | Same as SHAPEWIN
T17 | DOUBLE | h | Time point 17 |  | Same as SHAPEWIN
I17 | DOUBLE | p.u. | Load at time point 17 |  | Same as SHAPEWIN
T18 | DOUBLE | h | Time point 18 |  | Same as SHAPEWIN
I18 | DOUBLE | p.u. | Load at time point 18 |  | Same as SHAPEWIN
T19 | DOUBLE | h | Time point 19 |  | Same as SHAPEWIN
I19 | DOUBLE | p.u. | Load at time point 19 |  | Same as SHAPEWIN
T20 | DOUBLE | h | Time point 20 |  | Same as SHAPEWIN
I20 | DOUBLE | p.u. | Load at time point 20 |  | Same as SHAPEWIN
T21 | DOUBLE | h | Time point 21 |  | Same as SHAPEWIN
I21 | DOUBLE | p.u. | Load at time point 21 |  | Same as SHAPEWIN
T22 | DOUBLE | h | Time point 22 |  | Same as SHAPEWIN
I22 | DOUBLE | p.u. | Load at time point 22 |  | Same as SHAPEWIN
T23 | DOUBLE | h | Time point 23 |  | Same as SHAPEWIN
I23 | DOUBLE | p.u. | Load at time point 23 |  | Same as SHAPEWIN
SHAPETYPE | SMALLINT |  | Shape type code |  | Same as SHAPEWIN
LOADFACT | DOUBLE |  | Load factor |  | Same as SHAPEWIN
PEAKAMPS | DOUBLE | A | Peak amps for this shape |  | Historical peak current
HISTORICAL_DATA_FLAG | SMALLINT |  | Historical data flag |  | Whether this is archived historical data
TAG | VARCHAR |  | Record tag |  | Internal flag
LOCKEDBY | VARCHAR |  | Locked by user |  | Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Multi-user locking timestamp

## JOBSTEMPLATE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — unique identifier |  | Same as STUDYHED.IDSTUDY; Primary key, VARCHAR
EXECUNO | SMALLINT |  | Execution number within study |  | Same as STUDYHED.EXECUNO; Sub-case identifier within study
STUDYTITLE | VARCHAR |  | Study title |  | Same as STUDYHED.STUDYTITLE; User-entered study description
EXECDATE | VARCHAR |  | Execution date |  | Same as STUDYHED.EXECDATE; Date of calculation run
COMMENTS | VARCHAR |  | Study comments |  | Same as STUDYHED.COMMENTS; User-entered notes
EXECUTITLE | VARCHAR |  | Execution title |  | Same as STUDYHED.EXECUTITLE; User-entered sub-case description
TAG | VARCHAR |  | Record tag |  | Same as STUDYHED.TAG; Internal flag
TAG2 | VARCHAR |  | Secondary record tag |  | Same as STUDYHED.TAG2; Internal flag
MODECALC | SMALLINT |  | Calculation mode | Calculation mode code | Same as STUDYHED.MODECALC; Which calculation method to use
NCABLE | SMALLINT |  | Number of cables in study |  | Same as STUDYHED.NCABLE; Count of cable positions
NTYPE | SMALLINT |  | Number of cable types |  | Same as STUDYHED.NTYPE; Distinct cable designs used
AMBIENT | DOUBLE | °C | Ambient soil/air temperature |  | Same as STUDYHED.AMBIENT; IEC 60287 ambient temperature
RHOS | DOUBLE | K.m/W | Native soil thermal resistivity |  | Same as STUDYHED.RHOS; IEC 60287 soil thermal resistivity
IREFCA | SMALLINT | A | Reference cable current |  | Same as STUDYHED.IREFCA; Initial/reference current for iteration
XB | DOUBLE | m | Drawing X boundary (GUI) |  | Same as STUDYHED.XB; Cross-section view boundary
YB | DOUBLE | m | Drawing Y boundary (GUI) |  | Same as STUDYHED.YB; Cross-section view boundary
ALB | DOUBLE |  | Drawing scale parameter (GUI) |  | Same as STUDYHED.ALB; Cross-section view scale
AXB | DOUBLE |  | Drawing axis parameter (GUI) |  | Same as STUDYHED.AXB; Cross-section view axis
RHOB | DOUBLE | K.m/W | Backfill thermal resistivity |  | Same as STUDYHED.RHOB; Thermal resistivity of installed backfill
CABINAIR | VARCHAR |  | Cable in air flag |  | Same as STUDYHED.CABINAIR; Whether any cables are in air
EXTHEAT | VARCHAR | W/m | External heat source rate |  | Same as STUDYHED.EXTHEAT; External heat dissipation per unit length
TEMTOL | DOUBLE | °C | Temperature convergence tolerance |  | Same as STUDYHED.TEMTOL; Solver convergence criterion
AMPTOL | DOUBLE | A | Ampacity convergence tolerance |  | Same as STUDYHED.AMPTOL; Solver convergence criterion
MAXNIT | SMALLINT |  | Maximum iterations |  | Same as STUDYHED.MAXNIT; Solver iteration limit
TRTOL | DOUBLE |  | Transient tolerance |  | Same as STUDYHED.TRTOL; Transient solver convergence criterion
TRSTEP | DOUBLE | s | Transient time step |  | Same as STUDYHED.TRSTEP; Transient solver time step
TRMAXNIT | SMALLINT |  | Transient max iterations |  | Same as STUDYHED.TRMAXNIT; Transient solver iteration limit
FRACT | DOUBLE |  | Load fraction |  | Same as STUDYHED.FRACT; Fraction of full load for calculation
FREQ | DOUBLE | Hz | System frequency |  | Same as STUDYHED.FREQ; 50 or 60 Hz for AC loss calculations
PRINTI | SMALLINT |  | Print intermediate results flag |  | Same as STUDYHED.PRINTI; Output control
PRINT | SMALLINT |  | Print results flag |  | Same as STUDYHED.PRINT; Output control
EXRESMO | SMALLINT |  | Extended results mode |  | Same as STUDYHED.EXRESMO; Output detail level
CAAIRAR | SMALLINT |  | Cable in air arrangement |  | Same as STUDYHED.CAAIRAR; Configuration for cables in air
SHADED | SMALLINT |  | Shaded/direct sunlight flag |  | Same as STUDYHED.SHADED; Solar radiation exposure
SUNINTEN | DOUBLE | W/m² | Solar radiation intensity |  | Same as STUDYHED.SUNINTEN; IEC 60287 solar radiation
SUNABSO | DOUBLE |  | Solar absorptivity coefficient |  | Same as STUDYHED.SUNABSO; Cable surface solar absorptivity
HEORTE | SMALLINT |  | Heat source or temperature boundary |  | Same as STUDYHED.HEORTE; Boundary condition type
HEATEMP | DOUBLE | °C | Heat source temperature |  | Same as STUDYHED.HEATEMP; Fixed temperature boundary
XLHEAT | DOUBLE | m | Heat source X position |  | Same as STUDYHED.XLHEAT; X coordinate of external heat source
YLHEAT | DOUBLE | m | Heat source Y position |  | Same as STUDYHED.YLHEAT; Y coordinate of external heat source
TR_HEATSRC | VARCHAR |  | Transient heat source flag |  | Same as STUDYHED.TR_HEATSRC; Whether heat source varies with time
HEATSRC_ID | VARCHAR |  | Heat source library ID |  | Same as STUDYHED.HEATSRC_ID; FK to HEATSRCLIB
HEATSRC_SF | DOUBLE |  | Heat source scale factor |  | Same as STUDYHED.HEATSRC_SF; Multiplier on library heat rate
DIAHEAT | DOUBLE | m | Heat source diameter |  | Same as STUDYHED.DIAHEAT; Physical size of external heat source
AMBAIR | SMALLINT | °C | Ambient air temperature |  | Same as STUDYHED.AMBAIR; For cable sections in air
CONVCO | SMALLINT | W/(m²·K) | Convection coefficient |  | Same as STUDYHED.CONVCO; For cable-in-air heat transfer
DUCT | VARCHAR |  | Duct flag |  | Same as STUDYHED.DUCT; Whether installation uses ducts
MIGFLAG | VARCHAR |  | Moisture migration flag |  | Same as STUDYHED.MIGFLAG; Whether to model dry-out zone
RHDX | DOUBLE | K.m/W | Dry zone thermal resistivity |  | Same as STUDYHED.RHDX; Soil resistivity in dried-out zone
ISOT | VARCHAR |  | Isothermal surface flag |  | Same as STUDYHED.ISOT; Boundary condition setting
RBOX | DOUBLE |  | Result box display flag (GUI) |  | Same as STUDYHED.RBOX; GUI display option
TRANOPT | SMALLINT |  | Transient option |  | Same as STUDYHED.TRANOPT; Transient calculation sub-option
IOP | SMALLINT |  | Iterative optimisation parameter |  | Same as STUDYHED.IOP; Solver tuning
STARTVAL | DOUBLE |  | Parameter sweep start value |  | Same as STUDYHED.STARTVAL; For parametric studies
ENDVAL | DOUBLE |  | Parameter sweep end value |  | Same as STUDYHED.ENDVAL; For parametric studies
STEP | DOUBLE |  | Parameter sweep step |  | Same as STUDYHED.STEP; For parametric studies
ENERGRATE | DOUBLE |  | Energy rate (economic analysis) |  | Same as STUDYHED.ENERGRATE; Cost per kWh
DISCRATE | DOUBLE | % | Discount rate (economic analysis) |  | Same as STUDYHED.DISCRATE; NPV discount rate
ENERCOST | DOUBLE |  | Energy cost (economic analysis) |  | Same as STUDYHED.ENERCOST; Total energy cost
DEMDCOST | DOUBLE |  | Demand cost (economic analysis) |  | Same as STUDYHED.DEMDCOST; Peak demand charge
LINCOST | DOUBLE |  | Linear cost (economic analysis) |  | Same as STUDYHED.LINCOST; Per-metre cable cost
ECONLIFE | DOUBLE | years | Economic life (economic analysis) |  | Same as STUDYHED.ECONLIFE; Design lifetime
INITINVEST | VARCHAR |  | Initial investment (economic analysis) |  | Same as STUDYHED.INITINVEST; Capital cost
LENGTH | DOUBLE | m | Cable route length |  | Same as STUDYHED.LENGTH; Total cable route length
CHARGING | VARCHAR | A | Charging current |  | Same as STUDYHED.CHARGING; Capacitive charging current
INITCURNT | DOUBLE | A | Initial current |  | Same as STUDYHED.INITCURNT; Starting current for time-varying analysis
LOADGROWTH | DOUBLE | %/yr | Load growth rate |  | Same as STUDYHED.LOADGROWTH; Annual load growth
ULTIMLF | DOUBLE |  | Ultimate load factor |  | Same as STUDYHED.ULTIMLF; Long-term target load factor
GROWTHYEAR | DOUBLE | years | Growth period |  | Same as STUDYHED.GROWTHYEAR; Years over which load grows
WIND | DOUBLE | m/s | Wind speed |  | Same as STUDYHED.WIND; For cable-in-air convection
WLENGTH | DOUBLE | m | Wavelength parameter |  | Same as STUDYHED.WLENGTH; For electromagnetic calculation
PERMTR | DOUBLE |  | Perimeter parameter |  | Same as STUDYHED.PERMTR; For tunnel/trough calculations
INSTTYPE | SMALLINT |  | Installation type code | 1=Underground, 2=Submarine, etc. | Same as STUDYHED.INSTTYPE; Underground, submarine, air, etc.
DUCTBANK | SMALLINT |  | Duct bank flag |  | Same as STUDYHED.DUCTBANK; Whether duct bank is used
DUCTBANKID | VARCHAR |  | Duct bank library ID reference |  | Same as STUDYHED.DUCTBANKID; Links to DUCTLIB table
DUCTYPOS | SMALLINT | m | Duct bank Y position (depth) |  | Same as STUDYHED.DUCTYPOS; Depth to duct bank reference point
RHD | DOUBLE | K.m/W | Duct material thermal resistivity |  | Same as STUDYHED.RHD; Study-level duct thermal resistivity
DUCTNAME | VARCHAR |  | Duct bank name |  | Same as STUDYHED.DUCTNAME; Display name
OFFSETX | DOUBLE | m | Duct bank X offset |  | Same as STUDYHED.OFFSETX; Horizontal offset of duct bank
OFFSETY | DOUBLE | m | Duct bank Y offset |  | Same as STUDYHED.OFFSETY; Vertical offset of duct bank
OFFSETX2 | DOUBLE | m | Duct bank X offset (secondary) |  | Same as STUDYHED.OFFSETX2; For two-bank configurations
OFFSETY2 | DOUBLE | m | Duct bank Y offset (secondary) |  | Same as STUDYHED.OFFSETY2; For two-bank configurations
DISTX | DOUBLE | m | Duct X spacing |  | Same as STUDYHED.DISTX; Horizontal distance between ducts
DISTY | DOUBLE | m | Duct Y spacing |  | Same as STUDYHED.DISTY; Vertical distance between ducts
TOTROW | SMALLINT |  | Total duct rows |  | Same as STUDYHED.TOTROW; Duct bank row count
TOTCOL | SMALLINT |  | Total duct columns |  | Same as STUDYHED.TOTCOL; Duct bank column count
DUPIINDI | DOUBLE | m | Duct inside diameter (study-level) |  | Same as STUDYHED.DUPIINDI; Study override for duct ID
DUPIOTDI | DOUBLE | m | Duct outside diameter (study-level) |  | Same as STUDYHED.DUPIOTDI; Study override for duct OD
MOISTURE | DOUBLE | % | Critical moisture content |  | Same as STUDYHED.MOISTURE; Threshold for moisture migration
TRANSIENT | VARCHAR |  | Transient analysis flag |  | Same as STUDYHED.TRANSIENT; Whether transient is enabled
OPTICALC | SMALLINT |  | Optimisation calculation flag |  | Same as STUDYHED.OPTICALC; Whether to optimise
OPTICIRCNO | SMALLINT |  | Optimisation circuit number |  | Same as STUDYHED.OPTICIRCNO; Which circuit to optimise
CHOTE_COMPATIBLE | VARCHAR |  | CHOTE compatibility flag |  | Same as STUDYHED.CHOTE_COMPATIBLE; Compatibility with CHOTE format
LOCKEDBY | VARCHAR |  | Locked by user |  | Same as STUDYHED.LOCKEDBY; Multi-user locking field
LOCKTSTAMP | VARCHAR |  | Lock timestamp |  | Same as STUDYHED.LOCKTSTAMP; Multi-user locking timestamp
AutoRefCircuitFlag | SMALLINT |  | Auto-reference circuit flag |  | Same as STUDYHED.AutoRefCircuitFlag; Automatic reference circuit selection
CHOTE_TIMELINE_DATE | VARCHAR |  | CHOTE timeline date |  | Same as STUDYHED.CHOTE_TIMELINE_DATE; Timeline reference date
HEATSOURCE_INSULATION_FLAG | INTEGER |  | Heat source insulation flag |  | Same as STUDYHED.HEATSOURCE_INSULATION_FLAG; Whether heat source has insulation
INSUDIAM_HEATSOURCE | DOUBLE | m | Heat source insulation diameter |  | Same as STUDYHED.INSUDIAM_HEATSOURCE; Insulation OD of heat source
THRESIS_HEATSOURCE | DOUBLE | K.m/W | Heat source insulation thermal resistivity |  | Same as STUDYHED.THRESIS_HEATSOURCE; Insulation of heat source
POWERFACTOR | DOUBLE |  | Power factor |  | Same as STUDYHED.POWERFACTOR; For AC power calculation
LAGGING_LEADING_FLAG | INTEGER |  | Lagging/leading power factor flag |  | Same as STUDYHED.LAGGING_LEADING_FLAG; 0=Lagging, 1=Leading
TUNNEL_IMAGE_CHOSEN | INTEGER |  | Tunnel image selection (GUI) |  | Same as STUDYHED.TUNNEL_IMAGE_CHOSEN; GUI display
TUNNEL_CABLETYPE_CHOSEN | INTEGER |  | Tunnel cable type selection |  | Same as STUDYHED.TUNNEL_CABLETYPE_CHOSEN; Cable arrangement in tunnel
TUNNEL_DIAM | DOUBLE | m | Tunnel diameter |  | Same as STUDYHED.TUNNEL_DIAM; For tunnel installation
TUNNEL_ESTHECTIC_PARAM | INTEGER |  | Tunnel aesthetic parameter (GUI) |  | Same as STUDYHED.TUNNEL_ESTHECTIC_PARAM; GUI display
CYCLIC_LOADING | INTEGER |  | Cyclic loading flag |  | Same as STUDYHED.CYCLIC_LOADING; Whether cyclic loading is applied
EMF_XMIN | DOUBLE | m | EMF calculation X minimum |  | Same as STUDYHED.EMF_XMIN; EMF field calculation range
EMF_XMAX | DOUBLE | m | EMF calculation X maximum |  | Same as STUDYHED.EMF_XMAX; EMF field calculation range
EMF_XSTEP | DOUBLE | m | EMF calculation X step |  | Same as STUDYHED.EMF_XSTEP; EMF field calculation resolution
EMF_YVALUES | VARCHAR |  | EMF Y values (serialized) |  | Same as STUDYHED.EMF_YVALUES; EMF field Y coordinates
TF_LEVEL_VALUES | VARCHAR |  | Temperature field contour levels |  | Same as STUDYHED.TF_LEVEL_VALUES; Thermal field visualisation
TF_LEVEL_COLORS | VARCHAR |  | Temperature field contour colours |  | Same as STUDYHED.TF_LEVEL_COLORS; Thermal field visualisation
TF_LABEL_SPACING | INTEGER |  | Temperature field label spacing |  | Same as STUDYHED.TF_LABEL_SPACING; Thermal field visualisation
TF_RESOLUTION | DOUBLE |  | Temperature field resolution |  | Same as STUDYHED.TF_RESOLUTION; Thermal field grid resolution
TF_ZOOMOUT_POSITION | INTEGER |  | Temperature field zoom position (GUI) |  | Same as STUDYHED.TF_ZOOMOUT_POSITION; GUI display
TG_FRAME_LEFTPOS | DOUBLE | m | Trough/gutter frame left position |  | Same as STUDYHED.TG_FRAME_LEFTPOS; Trough geometry
TG_FRAME_TOPPOS | DOUBLE | m | Trough/gutter frame top position |  | Same as STUDYHED.TG_FRAME_TOPPOS; Trough geometry
TG_FRAME_WIDTH | DOUBLE | m | Trough/gutter frame width |  | Same as STUDYHED.TG_FRAME_WIDTH; Trough geometry
TG_FRAME_HEIGHT | DOUBLE | m | Trough/gutter frame height |  | Same as STUDYHED.TG_FRAME_HEIGHT; Trough geometry
TG_FRAME_THRESIS | DOUBLE | K.m/W | Trough/gutter frame thermal resistivity |  | Same as STUDYHED.TG_FRAME_THRESIS; Trough material
TG_INSIDE_TEXTURE | INTEGER |  | Trough inside texture (GUI) |  | Same as STUDYHED.TG_INSIDE_TEXTURE; GUI display
TG_FRAME_TEXTURE | INTEGER |  | Trough frame texture (GUI) |  | Same as STUDYHED.TG_FRAME_TEXTURE; GUI display
CROSSINGS_FLAG | VARCHAR |  | Cable crossings flag |  | Same as STUDYHED.CROSSINGS_FLAG; Whether cable crossings are modelled
HEATSOURCE_COLD_OR_HOT | INTEGER |  | Heat source hot/cold flag |  | Same as STUDYHED.HEATSOURCE_COLD_OR_HOT; Whether source heats or cools
CASINGID | VARCHAR |  | Casing library ID |  | Same as STUDYHED.CASINGID; FK to CASINGLIB
MULTCASING_INSTALLATION_TYPE | INTEGER |  | Multiple casing installation type |  | Same as STUDYHED.MULTCASING_INSTALLATION_TYPE; Configuration
DEPTH_OF_SEABED | DOUBLE | m | Depth of seabed |  | Same as STUDYHED.DEPTH_OF_SEABED; For submarine cable installation
EARTH_RESISTIVITY | DOUBLE | ohm.m | Earth electrical resistivity |  | Same as STUDYHED.EARTH_RESISTIVITY; For grounding calculations
COMMON_FREQUENCY_FLAG | INTEGER |  | Common frequency flag |  | Same as STUDYHED.COMMON_FREQUENCY_FLAG; Whether all cables share same frequency
CABLE_RESISTANCE_FLAG | INTEGER |  | Cable resistance calculation flag |  | Same as STUDYHED.CABLE_RESISTANCE_FLAG; How AC resistance is computed
USE_ENLARGE_BOUNDARIES | VARCHAR |  | Enlarged boundaries flag |  | Same as STUDYHED.USE_ENLARGE_BOUNDARIES; FEM boundary extension
ENLARGE_BOUNDARIES_VALUE | DOUBLE |  | Enlarged boundaries value |  | Same as STUDYHED.ENLARGE_BOUNDARIES_VALUE; FEM boundary multiplier
ELECTRICAL_INTERATIVE_BETWEEN_CCTS | VARCHAR |  | Electrical interaction between circuits flag |  | Same as STUDYHED.ELECTRICAL_INTERATIVE_BETWEEN_CCTS; Inter-circuit coupling
TG_SHALLOW_TROUGHS_METHOD | INTEGER |  | Shallow troughs calculation method |  | Same as STUDYHED.TG_SHALLOW_TROUGHS_METHOD; IEC method selection
CUSTOM_GENERAL_RATINGS_FLAG | INTEGER |  | Custom general ratings flag |  | Same as STUDYHED.CUSTOM_GENERAL_RATINGS_FLAG; Override standard ratings
CABLEPARTS_TO_ITERATE_FLAG | INTEGER |  | Cable parts iteration flag |  | Same as STUDYHED.CABLEPARTS_TO_ITERATE_FLAG; Which parts to iterate on
DUCTBANK_CUSTOM_U | DOUBLE |  | Custom duct bank parameter U |  | Same as STUDYHED.DUCTBANK_CUSTOM_U; Custom thermal coefficient
DUCTBANK_CUSTOM_V | DOUBLE |  | Custom duct bank parameter V |  | Same as STUDYHED.DUCTBANK_CUSTOM_V; Custom thermal coefficient
DUCTBANK_CUSTOM_Y | DOUBLE |  | Custom duct bank parameter Y |  | Same as STUDYHED.DUCTBANK_CUSTOM_Y; Custom thermal coefficient
STD_NOMINAL_DUCT | INTEGER |  | Standard nominal duct size |  | Same as STUDYHED.STD_NOMINAL_DUCT; Nominal duct designation
CLEARANCES_MODE | INTEGER |  | Clearances calculation mode |  | Same as STUDYHED.CLEARANCES_MODE; How clearances are computed
TF_STEP_RESOLUTION | DOUBLE |  | Temperature field step resolution |  | Same as STUDYHED.TF_STEP_RESOLUTION; FEM mesh refinement
MEDIUM_DUCT_FLAG | INTEGER |  | Medium duct flag |  | Same as STUDYHED.MEDIUM_DUCT_FLAG; Duct fill medium type
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property calculation flag |  | Same as STUDYHED.MAGNETIC_PROPERTY_FLAG; Include magnetic effects
COND_TEMP_OVERLIMIT_FLAG | INTEGER |  | Conductor temperature over-limit flag |  | Same as STUDYHED.COND_TEMP_OVERLIMIT_FLAG; Warning/constraint
TUNNEL_VENTILATED_FLAG | INTEGER |  | Tunnel ventilation flag |  | Same as STUDYHED.TUNNEL_VENTILATED_FLAG; Whether tunnel has forced air
AIR_VELOCITY_IN_TUNNEL | DOUBLE | m/s | Air velocity in tunnel |  | Same as STUDYHED.AIR_VELOCITY_IN_TUNNEL; Forced ventilation speed
TEMP_OF_AIR_IN_TUNNEL | DOUBLE | °C | Air temperature in tunnel |  | Same as STUDYHED.TEMP_OF_AIR_IN_TUNNEL; Inlet air temperature
LENGTH_OF_TUNNEL | DOUBLE | m | Tunnel length |  | Same as STUDYHED.LENGTH_OF_TUNNEL; Total tunnel length
SHAPE_OF_TUNNEL | INTEGER |  | Tunnel cross-section shape |  | Same as STUDYHED.SHAPE_OF_TUNNEL; Circular, rectangular, etc.
INNER_DIAM_OF_TUNNEL | DOUBLE | m | Inner diameter of tunnel |  | Same as STUDYHED.INNER_DIAM_OF_TUNNEL; For circular tunnels
IEC_SCOPE_EXTENDED_FLAG | INTEGER |  | IEC extended scope flag |  | Same as STUDYHED.IEC_SCOPE_EXTENDED_FLAG; Whether extended IEC methods are used
RAC_FACTOR_MAGNETIC_DUCT | DOUBLE |  | AC resistance factor for magnetic duct |  | Same as STUDYHED.RAC_FACTOR_MAGNETIC_DUCT; Correction factor
DUCT_FILLING_TH_RESIS | DOUBLE | K.m/W | Duct filling thermal resistivity |  | Same as STUDYHED.DUCT_FILLING_TH_RESIS; Thermal resistivity of duct fill
MDB_DUCTS_TREFOIL_RECALC_FLAG | INTEGER |  | Duct trefoil recalculation flag |  | Same as STUDYHED.MDB_DUCTS_TREFOIL_RECALC_FLAG; Force recalculation
COMPUTE_SOLAR_RADIATION_FLAG | INTEGER |  | Compute solar radiation flag |  | Same as STUDYHED.COMPUTE_SOLAR_RADIATION_FLAG; Whether to include solar heating
SUNINTEN_PERPENDICULAR | DOUBLE | W/m² | Perpendicular solar radiation intensity |  | Same as STUDYHED.SUNINTEN_PERPENDICULAR; Solar flux normal to cable
ANGLE_INCIDENCE | INTEGER | ° | Angle of solar incidence |  | Same as STUDYHED.ANGLE_INCIDENCE; Sun angle to cable surface
FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR_FLAG | INTEGER |  | RAC magnetic armour factor flag |  | Same as STUDYHED.FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR_FLAG; IEC correction flag
FACTOR_RAC_DUE_TO_MAGNETIC_DUCT_FLAG | INTEGER |  | RAC magnetic duct factor flag |  | Same as STUDYHED.FACTOR_RAC_DUE_TO_MAGNETIC_DUCT_FLAG; IEC correction flag
FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR_FLAG | INTEGER |  | Lambda1 magnetic armour factor flag |  | Same as STUDYHED.FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR_FLAG; IEC correction flag
FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT_FLAG | INTEGER |  | Lambda1 magnetic duct factor flag |  | Same as STUDYHED.FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT_FLAG; IEC correction flag
FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING_FLAG | INTEGER |  | Lambda2-to-lambda1 circulating factor flag |  | Same as STUDYHED.FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING_FLAG; IEC correction flag
LAMBDA1_EDDY_COMPUTATION_FLAG | INTEGER |  | Lambda1 eddy current computation flag |  | Same as STUDYHED.LAMBDA1_EDDY_COMPUTATION_FLAG; IEC loss calculation method
LAMBDA2_PIPE_COMPUTATION_FLAG | INTEGER |  | Lambda2 pipe computation flag |  | Same as STUDYHED.LAMBDA2_PIPE_COMPUTATION_FLAG; IEC loss calculation method
WD_COMPUTATION_FLAG | INTEGER |  | Wd (dielectric loss) computation flag |  | Same as STUDYHED.WD_COMPUTATION_FLAG; IEC loss calculation method
T4_COMPUTATION_FLAG | INTEGER |  | T4 (external thermal resistance) computation flag |  | Same as STUDYHED.T4_COMPUTATION_FLAG; IEC method
CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR | DOUBLE |  | Custom RAC factor for magnetic armour |  | Same as STUDYHED.CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_ARMOUR; User override value
CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_DUCT | DOUBLE |  | Custom RAC factor for magnetic duct |  | Same as STUDYHED.CUSTOM_FACTOR_RAC_DUE_TO_MAGNETIC_DUCT; User override value
CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR | DOUBLE |  | Custom lambda1 factor for magnetic armour |  | Same as STUDYHED.CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_ARMOUR; User override value
CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT | DOUBLE |  | Custom lambda1 factor for magnetic duct |  | Same as STUDYHED.CUSTOM_FACTOR_ON_LAMBDA1_DUE_TO_MAGNETIC_DUCT; User override value
CUSTOM_FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING | DOUBLE |  | Custom lambda2-to-lambda1 circulating factor |  | Same as STUDYHED.CUSTOM_FACTOR_ON_LAMBDA2_ARMOUR_TO_LAMBDA1_CIRCULATING; User override value
GENERAL_GUIDANCE_FLAG | INTEGER |  | General guidance/notes flag |  | Same as STUDYHED.GENERAL_GUIDANCE_FLAG; Whether guidance notes are shown
T2_COMPUTATION_FLAG | INTEGER |  | T2 (between sheath and armour) computation flag |  | Same as STUDYHED.T2_COMPUTATION_FLAG; IEC method
ENVIRONMENT_CONFIG_ID | CHAR |  | Environment configuration ID |  | Same as STUDYHED.ENVIRONMENT_CONFIG_ID; FK to GLOBAL_ENVIRONMENT_PARAMETERS
ENVIRONMENT_OFFSET_AMBIENT | DOUBLE | °C | Ambient temperature offset |  | Same as STUDYHED.ENVIRONMENT_OFFSET_AMBIENT; Adjustment to environment config ambient
CABIN_JTUBE_FLAG | CHAR |  | Cable in J-tube flag |  | Same as STUDYHED.CABIN_JTUBE_FLAG; For J-tube installations
JTUBE_LENGTH_ABOVE_WATER | DOUBLE | m | J-tube length above water |  | Same as STUDYHED.JTUBE_LENGTH_ABOVE_WATER; Exposed J-tube section
CAB_IMMERSED_IN_WATER_FLAG | CHAR |  | Cable immersed in water flag |  | Same as STUDYHED.CAB_IMMERSED_IN_WATER_FLAG; Submarine section flag
HIGH_VOLTAGE_DC_CABLE_FLAG | CHAR |  | HVDC cable flag |  | Same as STUDYHED.HIGH_VOLTAGE_DC_CABLE_FLAG; For DC-specific calculations
TUNNELWALL_ADVANCED_FLAG | INTEGER |  | Advanced tunnel wall modelling flag |  | Same as STUDYHED.TUNNELWALL_ADVANCED_FLAG; Detailed wall thermal model
TUNNELWALL_THICKNESS | DOUBLE | m | Tunnel wall thickness |  | Same as STUDYHED.TUNNELWALL_THICKNESS; For wall thermal resistance
TUNNELWALL_THERMALRESIS | DOUBLE | K.m/W | Tunnel wall thermal resistivity |  | Same as STUDYHED.TUNNELWALL_THERMALRESIS; Wall material property

## MCPP
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — FK to STUDYHED |  | Parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case
CIRCUITNO | INTEGER |  | Circuit number |  | Which circuit for multi-cable per phase
ROWNO | INTEGER |  | Row number |  | Data row index
CURRENT_PHASEA | DOUBLE | A | Phase A current |  | Current in phase A
CURRENT_PHASEB | DOUBLE | A | Phase B current |  | Current in phase B
CURRENT_PHASEC | DOUBLE | A | Phase C current |  | Current in phase C
TAG | CHAR |  | Record tag |  | Internal flag

## MULTIPLELAYER_JOBSTEMPLATE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — foreign key to STUDYHED |  | Same as MULTIPLELAYER.IDSTUDY; Links to parent study
EXECUNO | DOUBLE |  | Execution number |  | Same as MULTIPLELAYER.EXECUNO; Sub-case identifier
TAG | VARCHAR |  | Record tag |  | Same as MULTIPLELAYER.TAG; Internal flag
LAYERNO | SMALLINT |  | Layer number (0-based) |  | Same as MULTIPLELAYER.LAYERNO; Index of this soil/backfill layer
LAYERTYPE | INTEGER |  | Layer type |  | Same as MULTIPLELAYER.LAYERTYPE; Soil, backfill, duct bank, etc.
LAYERNAME | VARCHAR |  | Layer display name |  | Same as MULTIPLELAYER.LAYERNAME; User-entered label
LAYERCAPTION | VARCHAR |  | Layer caption (GUI) |  | Same as MULTIPLELAYER.LAYERCAPTION; GUI display label
XLEFT | DOUBLE | m | Left edge X coordinate |  | Same as MULTIPLELAYER.XLEFT; Layer boundary
YTOP | DOUBLE | m | Top edge Y coordinate (depth) |  | Same as MULTIPLELAYER.YTOP; Layer boundary
XB | DOUBLE | m | Layer width |  | Same as MULTIPLELAYER.XB; Horizontal extent
YB | DOUBLE | m | Layer height |  | Same as MULTIPLELAYER.YB; Vertical extent
AXB | DOUBLE |  | Drawing axis parameter (GUI) |  | Same as MULTIPLELAYER.AXB; Cross-section display
AYB | DOUBLE |  | Drawing Y-axis parameter (GUI) |  | Same as MULTIPLELAYER.AYB; Cross-section display
DUCTYPOS | SMALLINT | m | Duct bank Y position within layer |  | Same as MULTIPLELAYER.DUCTYPOS; Depth of duct bank
DUCTBANKID | VARCHAR |  | Duct bank library ID |  | Same as MULTIPLELAYER.DUCTBANKID; FK to DUCTLIB
DUCTBANK | SMALLINT |  | Duct bank name |  | Same as MULTIPLELAYER.DUCTBANK; Display name
RHD | DOUBLE | K.m/W | Duct thermal resistivity |  | Same as MULTIPLELAYER.RHD; Duct material property
ALIGN_HOR | SMALLINT |  | Horizontal alignment (GUI) |  | Same as MULTIPLELAYER.ALIGN_HOR; GUI display
ALIGN_VER | SMALLINT |  | Vertical alignment (GUI) |  | Same as MULTIPLELAYER.ALIGN_VER; GUI display
LAYERCOLOR | SMALLINT |  | Layer colour code (GUI) |  | Same as MULTIPLELAYER.LAYERCOLOR; GUI display
LAYERRESIS | DOUBLE | K.m/W | Layer thermal resistivity |  | Same as MULTIPLELAYER.LAYERRESIS; Soil/backfill thermal resistivity
INSIDE_DIAM | DOUBLE | m | Casing inside diameter |  | Same as MULTIPLELAYER.INSIDE_DIAM; For casing within layer
OUTSIDE_DIAM | DOUBLE | m | Casing outside diameter |  | Same as MULTIPLELAYER.OUTSIDE_DIAM; For casing within layer
CASING_CONFIGURATION_TYPE | INTEGER |  | Casing configuration type |  | Same as MULTIPLELAYER.CASING_CONFIGURATION_TYPE; Casing arrangement
CASING_CONSTRUCTION_TYPE | INTEGER |  | Casing construction type |  | Same as MULTIPLELAYER.CASING_CONSTRUCTION_TYPE; Casing material/build
DUCT_ATTACHED_TO_CASING_INDEX | INTEGER |  | Index of duct attached to casing |  | Same as MULTIPLELAYER.DUCT_ATTACHED_TO_CASING_INDEX; Casing-duct linkage
SHAPETYPE | INTEGER |  | Layer shape type |  | Same as MULTIPLELAYER.SHAPETYPE; Cross-section shape (rectangular, trapezoidal, etc.)
FRAME_XCENTRE | DOUBLE | m | Frame X centre (GUI) |  | Same as MULTIPLELAYER.FRAME_XCENTRE; GUI frame position
FRAME_YCENTRE | DOUBLE | m | Frame Y centre (GUI) |  | Same as MULTIPLELAYER.FRAME_YCENTRE; GUI frame position
FRAME_XLEFT | DOUBLE | m | Frame left edge (GUI) |  | Same as MULTIPLELAYER.FRAME_XLEFT; GUI frame position
FRAME_YTOP | DOUBLE | m | Frame top edge (GUI) |  | Same as MULTIPLELAYER.FRAME_YTOP; GUI frame position
FRAME_WIDTH | DOUBLE | m | Frame width (GUI) |  | Same as MULTIPLELAYER.FRAME_WIDTH; GUI frame size
FRAME_HEIGHT | DOUBLE | m | Frame height (GUI) |  | Same as MULTIPLELAYER.FRAME_HEIGHT; GUI frame size
FRAME_LAYERCOLOR | INTEGER |  | Frame layer colour (GUI) |  | Same as MULTIPLELAYER.FRAME_LAYERCOLOR; GUI display
FRAME_LAYERRESIS | INTEGER | K.m/W | Frame layer thermal resistivity |  | Same as MULTIPLELAYER.FRAME_LAYERRESIS; Encasement material property
DUCTXPOS | INTEGER | m | Duct X position within layer |  | Same as MULTIPLELAYER.DUCTXPOS; Horizontal position of duct
LAYER_RESIS_SAME_AS_SOIL_RESIS_FLAG | INTEGER |  | Layer resistivity same as soil flag |  | Same as MULTIPLELAYER.LAYER_RESIS_SAME_AS_SOIL_RESIS_FLAG; Whether layer inherits soil properties
DUCT_CUSTOM_U | DOUBLE |  | Custom duct thermal parameter U |  | Same as MULTIPLELAYER.DUCT_CUSTOM_U; Custom thermal coefficient
DUCT_CUSTOM_V | DOUBLE |  | Custom duct thermal parameter V |  | Same as MULTIPLELAYER.DUCT_CUSTOM_V; Custom thermal coefficient
DUCT_CUSTOM_Y | DOUBLE |  | Custom duct thermal parameter Y |  | Same as MULTIPLELAYER.DUCT_CUSTOM_Y; Custom thermal coefficient
LD_ARROW_WIDTH_POSITION | INTEGER |  | Layer dimension arrow width position (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_WIDTH_POSITION; GUI dimension display
LD_ARROW_WIDTH_MARGIN | DOUBLE |  | Layer dimension arrow width margin (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_WIDTH_MARGIN; GUI dimension display
LD_ARROW_WIDTH_INSIDECOMPO_FLAG | INTEGER |  | Width arrow inside component flag (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_WIDTH_INSIDECOMPO_FLAG; GUI dimension display
LD_ARROW_HEIGHT_POSITION | INTEGER |  | Layer dimension arrow height position (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_HEIGHT_POSITION; GUI dimension display
LD_ARROW_HEIGHT_MARGIN | DOUBLE |  | Layer dimension arrow height margin (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_HEIGHT_MARGIN; GUI dimension display
LD_ARROW_HEIGHT_INSIDECOMPO_FLAG | INTEGER |  | Height arrow inside component flag (GUI) |  | Same as MULTIPLELAYER.LD_ARROW_HEIGHT_INSIDECOMPO_FLAG; GUI dimension display
MEDIUM_DUCT_FLAG | INTEGER |  | Medium duct flag |  | Same as MULTIPLELAYER.MEDIUM_DUCT_FLAG; Duct fill medium type
MAGNETIC_PROPERTY_FLAG | INTEGER |  | Magnetic property flag |  | Same as MULTIPLELAYER.MAGNETIC_PROPERTY_FLAG; Include magnetic effects
FRAME_LAYERRESIS_NEW | DOUBLE | K.m/W | Updated frame layer thermal resistivity |  | Same as MULTIPLELAYER.FRAME_LAYERRESIS_NEW; Updated encasement property
REAL_DUCTS_IN_TREFOIL_YCENTRE | DOUBLE | m | Real duct trefoil Y centre |  | Same as MULTIPLELAYER.REAL_DUCTS_IN_TREFOIL_YCENTRE; Actual trefoil position
DUCT_FILLING_TH_RESIS | DOUBLE | K.m/W | Duct filling thermal resistivity |  | Same as MULTIPLELAYER.DUCT_FILLING_TH_RESIS; Thermal resistivity of duct fill material
DUCT_IN_TREFOIL_RECALCULATED_FLAG | INTEGER |  | Duct trefoil recalculated flag |  | Same as MULTIPLELAYER.DUCT_IN_TREFOIL_RECALCULATED_FLAG; Whether trefoil positions were recalculated

## MULTIPLE_HEATSOURCE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | VARCHAR |  | Study ID — FK to STUDYHED |  | Parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case
HEATSRCNO | INTEGER |  | Heat source number |  | Index of heat source within study
HEORTE | INTEGER |  | Heat or temperature boundary type |  | Whether source is heat rate or fixed temperature
HEATEMP | DOUBLE | °C | Heat source temperature |  | Fixed temperature if temperature boundary
XLHEAT | DOUBLE | m | Heat source X position (label) |  | Label X coordinate
YLHEAT | DOUBLE | m | Heat source Y position (label) |  | Label Y coordinate
DIAHEAT | DOUBLE | m | Heat source diameter |  | Physical size of heat source
HEATSOURCE_INSULATION_FLAG | INTEGER |  | Heat source insulation flag |  | Whether heat source has insulation
INSUDIAM_HEATSOURCE | DOUBLE | m | Heat source insulation diameter |  | Insulation OD of heat source
THRESIS_HEATSOURCE | DOUBLE | K.m/W | Heat source insulation thermal resistivity |  | Insulation of heat source
HEATSOURCE_COLD_OR_HOT | INTEGER |  | Heat source hot/cold flag |  | Whether source heats or cools
HEATSRC_ID | VARCHAR |  | Heat source library ID |  | FK to HEATSRCLIB
HEATSRC_SF | DOUBLE |  | Heat source scale factor |  | Multiplier on library heat rate
TAG | VARCHAR |  | Record tag |  | Internal flag

## PS_SCENARIO
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — FK to STUDYHED |  | Parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case
SCENARIO_NO | INTEGER |  | Scenario sequence number |  | Ordering index
TITLE | CHAR |  | Scenario title |  | Label
TAG | CHAR |  | Record tag |  | Internal flag

## PS_SPECVALUES
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — FK to STUDYHED |  | Parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case
SCENARIO_NO | INTEGER |  | Scenario sequence number |  | FK to PS_SCENARIO
VARIABLE_NO | INTEGER |  | Variable sequence number |  | FK to PS_VARIABLE
COLUMN_NO | INTEGER |  | Column number in parameter grid |  | Grid position
ROW_NO | INTEGER |  | Row number in parameter grid |  | Grid position
KEY_VAL1 | CHAR |  | Key value 1 (parameter identifier) |  | First key for the parameter
KEY_VAL2 | CHAR |  | Key value 2 (parameter identifier) |  | Second key for the parameter
VALUE1 | CHAR |  | Parameter value 1 |  | First value for this scenario/variable
VALUE2 | CHAR |  | Parameter value 2 |  | Second value for this scenario/variable

## PS_VARIABLE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — FK to STUDYHED |  | Parent study
EXECUNO | INTEGER |  | Execution number |  | Sub-case
SCENARIO_NO | INTEGER |  | Scenario sequence number |  | FK to PS_SCENARIO
VARIABLE_NO | INTEGER |  | Variable sequence number |  | Ordering index
CATEGORY_ID | INTEGER |  | Variable category ID |  | Grouping category
VARIABLE_ID | INTEGER |  | Variable identifier string |  | User-visible variable ID
COLUMN_NO | INTEGER |  | Column number in parameter grid |  | Grid position
INPUT_TYPE | INTEGER |  | Input type code |  | How the variable is entered
KEY_VAL1 | CHAR |  | Key value 1 (parameter identifier) |  | First key
KEY_VAL2 | CHAR |  | Key value 2 (parameter identifier) |  | Second key
FROM_VALUE | CHAR |  | Range start value |  | Sweep start
TO_VALUE | CHAR |  | Range end value |  | Sweep end
STEP_VALUE | CHAR |  | Range step value |  | Sweep increment

## RTTR
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
IDSTUDY | CHAR |  | Study ID — FK to STUDYHED |  | Real-time thermal rating config
EXECUNO | INTEGER |  | Execution number |  | Sub-case
TAG | CHAR |  | Record tag |  | Internal flag
SECTION_FOLDER | CHAR |  | RTTR section/folder reference |  | Data source location
CALCULATION_TYPE | INTEGER |  | RTTR calculation type |  | Real-time calculation method
FIBER_LOCATION | INTEGER |  | Fibre optic location reference |  | DTS fibre sensor position
MAXIMUM_SOLVING_TIME_IN_SECONDS | DOUBLE | s | Maximum solving time |  | Solver timeout
CIRCUITNO | INTEGER |  | Circuit number |  | Which circuit for RTTR
ROWNO | INTEGER |  | Row number |  | Data row index
CURRENT_PHASEA | DOUBLE | A | Phase A current |  | Measured phase A current
CURRENT_PHASEB | DOUBLE | A | Phase B current |  | Measured phase B current
CURRENT_PHASEC | DOUBLE | A | Phase C current |  | Measured phase C current

## UNDELETE
Column Name | DB Type | Assumed Units | Description | Enum Values | Justification
ID | VARCHAR |  | Unique record identifier |  | Auto-increment ID
KEY | VARCHAR |  | Primary key of deleted record |  | For undo functionality
DATE | VARCHAR |  | Deletion date |  | When the record was deleted
TITLE | VARCHAR |  | Deleted record title/description |  | Summary of what was deleted
KEY2 | VARCHAR |  | Secondary key of deleted record |  | For composite-key tables